## Sheet1
EventNumber | Day | Month | Year | Geographical Location | Country | Industry | Facility | Site | Unit | Mode | INES | INES (guess) | Region | Description | Type | Status | Gross Electrical Capacity [MW] | Grid Connection Year | Comments (DB V3) | Core relevant | Origin_description | Origin (incl. potential origin in the case of a degraded system) | Cause_description | Cause (incl. potential cause) | Lower Limit | Upper Limit
2 | 13 | 5 | 2016 | Salem, United States | United States | Energy | Plant | SUSQUEHANNA | 2 | 2 |  | 1 | NA | The Supervisor directed manually overriding High Pressure Coolant Injection (HPCI) immediately prior to a manual scram during a plant transient; the potential consequence of overriding HPCI is, in the potential event of a small break loss of coolant accident, that operations would not be able to maintain adequate core cooling; no radiation impact. | BWR | Operational | 1330 | 1984 |  | ? |  | 1 |  | H | 0 | 0
5 | 28 | 3 | 2016 | Bento, United States | United States | Energy | Plant | COLUMBIA | Single | 2 |  | 0 | NA | A manual reactor scram was initiated in response to a loss of Reactor Closed Cooling (RCC) due to the opening of a service water valve at the inlet side of the fuel pool cooling heat exchanger during faulty performance of a partial surveillance. The loss of RCC resulted in a loss of cooling to several components, including the reactor recirculation pumps; all plant systems responded as designed. | BWR | Operational | 1190 | 1984 |  | ? |  | 1 |  | H? | 8 | 10
6 | 11 | 3 | 2016 | Surat, India | India | Energy | Plant | KAKRAPAR | 1,2 | 2 |  | 1 | A | The reactor was running at full power when the first leakage of steam was detected visually on remotely operated cameras; later as pressure rose in the containment a plant emergency was immediately declared; all safety systems worked well, the reactor was shut down and radioactivity confined in the reactor building. | PHWR | Operational | 220 | 1992;1995 |  | 0 |  | 1 |  | T | 600 | 1000
9 | 22 | 1 | 2016 | Lagoona Beach, United States | United States | Energy | Plant | FERMI | 2 | 0 |  | 1 | NA | Both divisions of the Residual Heat Removal System were declared inoperable for Low Pressure Coolant Injection (LPCI) mode due to a failure of the division 1 LPCI outboard injection valve to open after properly closing during an operability surveillance test. | BWR | Operational | 1198 | 1986 | probably minor contribution to CCDF | ? |  | 1 |  | T | 0 | 1
10 | 23 | 1 | 2016 | Oswego, United States | United States | Energy | Plant | FITZPATRICK | Single | 2 |  | 1 | NA | The plant was ascending in power when screenwell water level started to lower caused by frazil ice blockage at the intake structure. At 89 percent power, at 22:23, operators began taking compensatory measures to reduce power and mitigate water level lowering; 17 minutes later a manual scram was initiated, complicated by a residual transfer that resulted in non-vital equipment trips and finally led to manual actuation of some safety-related systems. | BWR | Operational | 849 | 1975 | technically interesting precursor, CCF | 1 |  | 3 |  | T | 12 | 16
11 | 18 | 12 | 2015 | Sosnovyy-Bor, Russia | Russia | Energy | Plant | LENINGRAD | 2 | 2 |  | 1 | EE | A pipe carrying steam from the reactor to the turbine-generator cracked in the turbine hall, releasing radioactive steam and forcing an evacuation of the facility after the reactor was manually scrammed. | LWGR | Operational | 1000 | 1975 |  | 0 |  | 2 |  | T | 1 | 10
12 | 14 | 12 | 2016 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 3 | 2 |  | 0 | NA | Automatic reactor trip due to a turbine-generator trip as a result of a fault on 345 kV feeder of a transmission tower, apparently caused by bird streaming; all control rods inserted and required safety systems functioned properly. | PWR | Operational | 1085 | 1976 | unplanned scram | 0 |  | 3 |  | T | 5 | 10
14 | 31 | 10 | 2015 | Doel, Belgium | Belgium | Energy | Plant | DOEL | 1 | 0 |  | NA | WE | An explosion/fire occurred at a transformer was extinguished by personnel. The reactor was shutdown and not in danger. | PWR | Operational | 454 | 1974 |  | 0 |  | 2 |  | T | 0 | 10
16 | 23 | 7 | 2015 | Pickering, Canada | Canada | Energy | Plant | PICKERING |  | 2 |  | 0 | NA | Staff at Pickering Nuclear discovered the incorrect blocking and locking of a valve that is part of the guaranteed shutdown system. | PHWR |  |  |  | event not further specific – apparently minor safety relevance - omit | 0 | Guaranteed shutdown system | 1 | Improper maintenance | H | 0 | 0
17 | 23 | 7 | 2015 | Fulton, United States | United States | Energy | Plant | CALLAWAY | 1 | 1 |  | 1 | NA | The plant was on the way from hot standby to cold shutdown mode, operating with one main feedwater pump when the the pump speed unexpectedly lowered to zero. After manual trip of the pump the water level in the steam generators decreased and the Manual Auxiliary Feedwater System was actuated. | PWR | Operational | 1275 | 1984 |  | 0 |  | 1 |  | T | 0 | 0
18 | 13 | 7 | 2015 | Daeniken, Switzerland | Switzerland | Energy | Plant | GOESGEN | Single | 1 | 1 | 1 | WE | During restart after turbine trip a combination of operator errors caused shutdown of two steam isolation valves followed by a system response as designed including reactor trip; restart the following day | PWR | Operational | 1060 | 1979 | INES 1 due to numerous similar operator errors before | 0 |  | 2 |  | H | 1 | 2
20 | 28 | 5 | 2015 | Cattenom, France | France | Energy | Plant | CATTENOM | 1 | 2 | 1 | 1 | WE | Unexpected opening of a secondary system valve resulted in an atmospheric steam release; reactor shutdown, steam generator remained undamaged. | PWR | Operational | 1362 | 1986 |  | 0 |  | 2 |  | T | 1 | 10
21 | 9 | 5 | 2015 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | 2 |  |  | NA | A steam leak in the turbine building forced the reactor to shut down until repairs could be made. The plant was brought back online and synchronized with the local power grid three days later. | PWR | Operational | 925 | 1977 |  | 0 |  | 2 |  | T | 5 | 10
22 | 9 | 5 | 2015 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 3 | 2 |  |  | NA | A transformer failed, causing the automated shutdown of the reactor. All control rods fully - inserted and all required safety systems functioned properly. A fire that resulted from the failure was extinguished, and the reactor was placed in a safe and stable condition. The failed transformer contained about 24,000 gallons of dielectric fluid, which is used as an insulator and coolant when the transformer is energized. The U.S. Coast Guard estimates that about 3,000 gallons of dielectric fluid entered the river following the failure. | PWR | Operational | 1085 | 1976 |  | 0 |  | 2 |  | T | 30 | 50
25 | 3 | 3 | 2015 | Byron, United States | United States | Energy | Plant | BYRON | 1 | 2 |  |  | NA | Reactor Trip Resulting from a Phase to Phase Fault on the 1E Main Power Transformer, caused by design vulnerability where ice falls from one component onto another. | PWR | Operational | 1242 | 1985 |  | 0 |  | 2 |  | T | 12 | 20
26 | 28 | 1 | 2015 | Hartsville, United States | United States | Energy | Plant | ROBINSON | 2 | 2 |  | 1 | NA | Both trains of the Reactor Protection System and DC electrical distribution system inoperable due to inadvertent parallel connection of both trains of these systems during refueling outage. | PWR | Operational | 780 | 1970 | Unclear if at full power with degraded safety system, and for how long | ? |  | 1 |  | H | 0 | 0
27 | 27 | 1 | 2015 | Plymouth, United States | United States | Energy | Plant | PILGRIM | 1 | 2 |  | 1 | NA | The plant underwent a storm-induced unplanned shutdown after the two 345 kV lines that provide off-site power tripped subsequently; a third off-site power line remained available, the emergency diesel generators were started successfully by way of precaution and the reactor was in safe shutdown condition. However, due to additional equipment failures, the regulator initiated special inspection. | BWR | Operational | 711 | 1972 | unplanned scram with some equipment issues | 1 |  | 3 |  | T | 10 | 20
29 | 28 | 12 | 2014 | Monticello, United States | United States | Energy | Plant | MONTICELLO | Single | 2 |  | 1 | NA | During surveillance test of one emergency diesel generator (EDG), a non-licensed operator erroneously adjusted the other EDG governor setting. Both EDGs were declared inoperable, although a subsequent evaluation determined that at least one EDG was always capable of performing its safety function. | BWR | Operational | 691 | 1971 | CCDF order of 10^-5 | 1 |  | 1 |  | H | 0 | 0
30 | 28 | 11 | 2014 | Enerhodar, Ukraine | Ukraine | Energy | Plant | ZAPOROZHYE | 3 | 2 | 0 | NA | EE | Disconnection of the plant from the power grid due to a failure of the electrical equipment in the turbine hall; restart 12/3/2014. | PWR | Operational | 1000 | 1986 |  | 0 |  | 2 |  | T | 10 | 20
31 | 25 | 11 | 2014 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | 2 |  | 0 | NA | As announced by the vendor, efficiency in loss of coolant accident analysis codes adversely affected predicted peak cladding temperature (2513 in excess of 2200 F); due to sufficient margins no impact on current operation and safety. | PWR | Operational | 925 | 1977 | anomaly, interesting case, CCF | ? |  | NA |  | T | 0 | 0
32 | 21 | 11 | 2014 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 7 | 0 |  | 1 | NA | During planned maintenance, a valve on the moderator system opened inside the reactor building. The leak was contained within the building and there was no impact to station staff, the public or the environment. | PHWR | Operational | 540 | 1984 |  | 0 |  | 1 |  | T | 0 | 1
33 | 1 | 11 | 2014 | Bridgman, United States | United States | Energy | Plant | COOK | 1,2 | 2 |  | 1 | NA | Manual reactor trip due to a storm induced heavy influx of dune grass and debris from Lake Michigan causing degraded forebay condition. | PWR | Operational | 1131;1231 | 1975;1978 | anomaly with two unexpected equipment issues, CCF | ? |  | 3 |  | T | 25 | 35
34 | 22 | 10 | 2014 | Killona, United States | United States | Energy | Plant | WATERFORD | 3 | 2 |  | 1 | NA | Visual inspection revealed holes in the fuel feed tanks of the emergency diesel generators; potential water intrusion could have rendered diesels inoperable. | PWR | Operational | 1250 | 1985 | INES 1 due to violation of safety culture, CCF | 0 |  | 3 |  | H | 0 | 10
35 | 17 | 10 | 2014 | Yeonggwang-gun, South Korea | South Korea | Energy | Plant | HANBIT | 3 | ? |  | ? | A | Delayed identification of steam generator tube leakage. | PWR | Operational | 1039 | 1994 |  | 0 |  | 1 |  | T | 280 | 500
37 | 11 | 8 | 2014 | Heysham, United Kingdom | United Kingdom | Energy | Plant | HEYSHAM | A1 | 2 |  | NA | WE | Unexpected cracking in the boiler spine of unit 1 at Heysham A forced an 8 week shutdown of four reactors in the Heysham A and Hartlepool sites; no direct safety impact. | GCR | Operational | 625 | 1983 |  | 0 |  | 1 |  | T | 350 | 600
39 | 5 | 8 | 2014 | Marseilles, United States | United States | Energy | Plant | LASALLE | 2 | 2 |  | 1 | NA | Reactor scram on high neutron flux followed by a "Group I containment isolation". One inboard isolation valve showed dual indication rather than fully closed. Troubleshooting determined a valve stem-disk separation which allowed the main disk to drop into the main steam flow path; the resulting pressure transient added positive reactivity which caused the high neutron flux scram. | BWR | Operational | 1207 | 1984 | technical failure (anomaly) with positive physical feedback | 0 |  | 1 |  | T | 25 | 35
40 | 24 | 6 | 2014 | Leibstadt, Switzerland | Switzerland | Energy | Plant | LEIBSTADT | Single | 2 | 1 | 1 | WE | Detection of a few boreholes through the steel wall of the primary containment without seriously impacting its integrity and retention capability. | BWR | Operational | 1275 | 1984 |  | 0 |  | NA |  | H | 0 | 1
41 | 25 | 5 | 2014 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 2,3 | 2 |  | 1 | NA | Dual unit reactor trip on loss of offsite power which occured in the main switchyard; all systems including the emergency diesel generators functioned as designed. | PWR | Operational | 918;1280 | 1975;1986 | Assumed technical | 1 |  | 2 |  | T | 23 | 30
42 | 19 | 5 | 2014 | Salem, United States | United States | Energy | Plant | SALEM | 2 | 2 |  | 0 | NA | A scheduled refueling outage was extended after 15 to 17 broken-off bolt heads from a cooling pump were found in the reactor vessel. Returned to service on July 11, 2014. | PWR | Operational | 1200 | 1981 |  | 0 |  | 1 |  | T | 120 | 160
45 | 9 | 4 | 2014 | Fessenheim, France | France | Energy | Plant | FESSENHEIM | 1 | 2 | 1 | 1 | WE | Internal flooding in the non-nuclear part of the reactor had damaged the safety electrical systems, leading to shutdown of reactor. The repair and requalification of the equipment affected by splashing water lasted nearly 50 days before the reactor was restarted. | PWR | Operational | 920 | 1977 |  | 0 |  | 2 |  | T | 60 | 100
46 | 21 | 1 | 2014 | Lusby, United States | United States | Energy | Plant | CALVERT CLIFFS | 1,2 | 2 |  | 2 | NA | Reactor tripped when a non-safety-related 13 kV service bus de-energized due to a ground fault on feeder breaker caused by inadequate protection against weather (snow storm) related water intrusion. The loss of the service bus caused the loss of circulating pumps and main condenser vacuum, requiring the use of auxiliary feedwater and atmospheric dump valves. Power was also lost to a safety-related bus which caused the start of the pertinent emergency diesel generator. | PWR | Operational | 918;911 | 1975;1976 | interesting precursor (Fukushima “postrunner”) | 1 |  | 3 |  | T | 15 | 25
50 | 9 | 12 | 2013 | Pope, United States | United States | Energy | Plant | ANO | 2 | 2 |  | 1 | NA | Unit taken offline due to a transformer fire in the site switchyard. The fire was contained without injuries or threats to safety. | PWR | Operational | 1065 | 1978 |  | 1 | Power supply: Unit Auxiliary Transformer | 2 | electrical fault; Improper installation | T;H | 50 | 80
53 | 8 | 10 | 2013 | Krsko, Slovenia | Slovenia | Energy | Plant | KRSKO | Single | 2 | 0 | 1 | EE | Discovery of three broken, and a few leaking, damaged fuel rods during unloading and fuel inspections, one additional pin broke during transfer; restarted expected at end of Nov. 2013. | PWR | Operational | 727 | 1981 |  | 0 |  | 1 |  | T | 12 | 20
54 | 6 | 10 | 2013 | Neckarwestheim, Germany | Germany | Energy | Plant | NECKARWESTHEIM | 2 | 0 | 1 | 1 | WE | False blockage of a checkvalve in one of the four trains of the decay heat removal system and concurrent clearing of another train for maintenance lead to temporary unavailability of the system to cope with external events. | PWR | Operational | 1400 | 1989 | Potential external trigger. | 0 |  | 3 |  | T | 0 | 0
56 | 22 | 8 | 2013 | Salem, United States | United States | Energy | Plant | SALEM | 1 | 2 |  | 1 | NA | Manual shut down after slightly radioactive water leaked out of from a valve in the rector coolant system and went through the plant's drain system as designed. The spill was confined to the plant's containment building; no risk to workers or the public, and regulators have said there was no risk to the public. | PWR | Operational | 1254 | 1976 | minor safety significance | 0 |  | 1 |  | T | 5 | 10
58 | 15 | 7 | 2013 | Shih-men Hsiang, Taiwan | Taiwan | Energy | Plant | CHINSHAN | 2 | 2 |  | 1 | A | Typhoon Soulik caused a generator and turbine trip, left seawater inlet blocked, damaged five filters and a traveling filter valve; reactor automatically shut down after manual power reduction failed; lengthy repairs. | BWR | Operational | 636 | 1978 |  | 1 |  | 3 |  | T | 3 | 5
59 | 23 | 6 | 2013 | Avila Beach, United States | United States | Energy | Plant | DIABLO CANYON | 1 | 1 |  | 1 | NA | Control room operators used an annunciator response procedure to address the loss of startup power. Contrary to technical specifications they made all three Unit 1 emergency diesel generators (EDG) inoperable for almost two minutes when they placed all EDG switches into manual control; all offsite and onsite power sources were operable. | PWR | Operational | 1197 | 1984 | human failure - lack of safety culture | 0 |  | 1 |  | H | 0 | 0
60 | 21 | 6 | 2013 | Kuosheng, Taiwan | Taiwan | Energy | Plant | KUOSHENG | 1 | 2 |  | 0 | A | Loose blade of the air damper fell onto the bus bar isolator between generator and main transformer and triggered automatic plant shutdown; no direct safety impact; resumed operation after a few (?) hours. | BWR | Operational | 985 | 1981 |  | ? |  | 2 |  | T | 2 | 4
62 | 30 | 5 | 2013 | Oesthammar, Sweden | Sweden | Energy | Plant | FORSMARK | 3 | 1 | 1 | 1 | NE | In refueling state the unit breakers of the 400kV incoming off site supply received an unintentional order to open, but only two out of three phases opened, causing low but still over 65% voltage in the rotation; no emergency diesel got start order; safety-grade components with phase imbalance protection were disconnected, due to over-heating; operability of grid supply and safety system re-established after 30 and 90 min, respectively; no off site consequences. | BWR | Operational | 1203 | 1985 |  | 1 |  | 2 |  | H | 0 | 1
63 | 3 | 5 | 2013 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | 2 |  | ? | NA | High Pressure Safety Injection (HPSI) System pump flow imbalance existing since commissioningl, as HPSI system flow and record loop injection valve positions was not adequately translated into design documents. Under worst case accident conditions, the HPSI system flow rates to the RCS loops could have been imbalanced resulting in less than 75% of the minimum required HPSI flow being injected into the reactor vessel, resulting in fuel overheating and damage. | PWR | Permanent Shutdown | 512 | 1973 | Potentially long term vulnerability. | 1 |  | 1 |  | T | 0 | 0
65 | 20 | 4 | 2013 | Hartlepool, United Kingdom | United Kingdom | Energy | Plant | HARTLEPOOL | A2 | 1 |  | 1 | WE | A small fire broke out in the turbine hall while the reactor was being brought back into service. The fire was caused by an oil leak, and ignited lagging surrounding part of the turbine. The reactor was shut down and cooled, mitigating any threat of nuclear contamination. Emergency services attended the fire from stations across the area and the fire was extinguished after roughly 35 minutes. | GCR | Operational | 655 | 1984 | minor safety significance | 0 |  | 2 |  | T | 5 | 10
66 | 17 | 4 | 2013 | Marseilles, United States | United States | Energy | Plant | LASALLE | 1,2 | 2 |  | 1 | NA | Lightning struck led to phase-to-ground faults resulting in an opening of the main switchyard and loss of offsite power and reactor scrams on both units. All emergency diesel generators started and loaded the respective busses, all control rods fully inserted and all systems responded as expected. | BWR | Operational | 1207 | 1982;1984 | Two unit precursor. | 1 |  | 3 |  | T | 50 | 80
68 | 20 | 3 | 2013 | Limerick, United States | United States | Energy | Plant | LIMERICK | 1 | 2 |  | ? | NA | The cause of the high pressure core injection system (HPCI) inoperability was a failure of a bellows actuated pressure switch which resulted in a significant turbine oil system leak. The apparent cause of the pressure switch bellows failure was corrosion fatigue. The potential safety consequence of this event is significant since the oil leak was of sufficient magnitude to have caused a loss of HPCI system injection capability during a design basis accident. however the reactor core isolation cooling (RCIC) system and low pressure emergency core cooling systems (ECCS) remained operable during the period when the HPCI system was rendered operable; the affected pressure switch is calibrated on a 6-year frequency. There is no preventive maintenance task that performs periodic replacement of the switch. The failed switch had been in service since initial plant operation. | BWR | Operational | 1194 | 1985 |  | 1 |  | 1 |  | T | 0 | 1
69 | 19 | 3 | 2013 | Kashiwazaki, Japan | Japan | Energy | Plant | KASHIWAZAKI KARIWA | 1 | 2 | 1 | 0-1 | A | In response to the discovery that bends were found in water rods at Unit 5 at Kashiwazaki-Kariwa (event on 16.10.2012), inspection of fuel assemblies was conducted for all units, and it was confirmed that some fuel rods touched each other in Unit 1. | BWR | Operational | 1100 | 1985 | anomaly - no contribution to CCDP | 0 |  | 1 |  | T | 0 | 0
71 | 1 | 1 | 2013 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 1 | 0 |  |  | NA | A fire broke out in a lube oil purification system in the Pickering Nuclear Unit 1 turbine hall. One of the three heating elements in the heater for the purification system remained energized when its associated switch was in the “off” Position. The fire caused extensive damage to the turbine lube oil purification skid and overhead cable trays, as well as ancillary damage to a nearby hydrogen system panel. Damage to the overhead cable trays led to 45 additional days of outage work for replacement | PHWR | Operational | 542 | 1971 |  | 0 |  | 2 |  | T | 30 | 100
72 | 12 | 12 | 2012 | Daisy, United States | United States | Energy | Plant | SEQUOYAH | 1,2 | 2 |  | 0-1 | NA | Both units were at risk of external flooding inundating the Unanalyzed Essential Raw Cooling Water pumping station through inadequate electrical conduit penetration seals that could allow flood waters to enter into the system at a rate greater than the installed sump pump capacity and impact system performance during a (hypothetical) flood event above plant grade. | PWR | Operational | 1221;1200 | 1980;1981 | Potential CCF | ? |  | 3 |  | T | 0 | 1
73 |  | 12 | 2012 | Romney Marsh, United Kingdom | United Kingdom | Energy | Plant | DUNGENESS | B1,B2 | 2 | 1 | 1 | WE | The primary sea defence (a shingle bank) was not as robust as previously thought. An investigation was initiated and the reactor had to shutdown whilst an improvement program was implemented. | GCR | Operational | 615 | 1983;1985 |  | 0 |  | 3 |  | T | 38 | 44
74 | 5 | 11 | 2012 | Romney Marsh, United Kingdom | United Kingdom | Energy | Plant | DUNGENESS | B2 | 3 | 1 | 1 | WE | Operator found that an incorrect control rod (less instead of more absorbative) had been loaded in March 2003. The misload was identified during routine control rod maintenance after their removal from the reactor. | GCR | Operational | 615 | 1985 | insignificant degradation of safety system | 0 |  | 1 |  | H | 0 | 0
75 | 24 | 10 | 2012 | Flamanville, France | France | Energy | Plant | FLAMANVILLE | 1 | 1 | 1 |  | WE | Leak on an auxiliary line of the reactor's coolant system, when entering the final restart phase, after planned shutdown; leak contained in the reactor building, and stopped by applying reactor cold shutdown instructions after 5 hours; no consequences for the staff nor the environment. | PWR | Operational | 1382 | 1985 |  | ? |  | 1 |  | T | 1 | 10
78 | 5 | 9 | 2012 | Paks, Hungary | Hungary | Energy | Plant | PAKS | 1 | 2 | 1 | 1 | EE | Fast-acting gate valve in the chilled water system switched-off for planned repair, and left open despite of regulations. | PWR | Operational | 500 | 1982 |  | ? |  | 1 |  | H | 0 | 0
82 | 20 | 5 | 2012 | Narora, India | India | Energy | Plant | NARORA | 1 | 0 | 1 | 0-1 | A | The operator, after completion of Emergency Core Cooling System (ECCS) monthly test, by mistake, initiated the ECCS during reactor cold shutdown state. The heavy water injection to Primary Heat Transport (PHT) system did not terminate as per logic and this led to entry of nitrogen gas into the PHT system. As a result of nitrogen ingress, core cooling flow in some of the coolant channels was disturbed. The operator immediately took corrective action to degas the PHT system and for restoration of normal flow through the core. | PHWR | Operational | 220 | 1989 | no impact on reactor safety as the reactor was under cold shutdown for about 8 days | 0 |  | 1 |  | H | 0 | 1
83 | 5 | 4 | 2012 | Penly, France | France | Energy | Plant | PENLY | 2 | 2 | 1 | 1 | WE | Oil fire started in the reactor building and was extinguished rapidly; the reactor was then automatically shutdown; abnormal water leak from a joint on the primary circuit, collected by dedicated circuits/tanks; incidental procedures; no impact on environment. | PWR | Operational | 1382 | 1992 |  | ? |  | 1 |  | T | 10 | 50
85 | 2 | 3 | 2012 | Leiston, United Kingdom | United Kingdom | Energy | Plant | SIZEWELL | B | 2 |  | 0 | WE | The reactor automatically shutdown following an electrical fault on the non nuclear side of the plant. One and a half weeks later it was restarted at half capacity with one turbine in operation. | PWR | Operational | 1250 | 1995 | unplanned scram - omit (?) | 0 |  | 2 |  | T | 20 | 30
86 | 16 | 2 | 2011 | Pierrelatte, France | France | Energy | Plant | TRICASTIN | 3,4 | 2 | 2 | 2 | WE | Potential failure of emergency diesel generators due to faster deterioration of pads to reduce friction between moving parts of diesel engines (detected before at another station). | PWR | Operational | 955 | 1981 | INES 2 due to potential common cause failure. Generic issue. Both internal and external triggers could lead to a demand on this degraded safety system. At all EDF sites, other than Tricastin NPP, where this type of bearing bushings exist (Blayais, Bugey, Chinon, Cruas, Dampierre, Gravelines, Saint-Laurent), each reactor has at least one back-up generator, in the reactor or on the site, equipped with a different brand of bearing bushing which do not have this defect. At those sites the anomaly is rated INES 1 by the ASN. | 1 |  | 1;3 |  | T | 0 | 10
87 | 31 | 1 | 2012 | San Clemente, United States | United States | Energy | Plant | SAN ONOFRE | 3 | 2 |  | 0 to 1 | NA | Small primary-to-secondary leak in one of the two steam generators; the leak was isolated and the reactor was rendered to cold shutdown conditions in accordance with plant procedures. The AIT report, 1 issued July 18, 2012, identified design control issues associated with the thermal-hydraulic modeling of the steam generators as the probable cause of the steam generator tube degradation that ultimately led to the tube leak in Unit 3. “ baseline core damage frequency of a steam generator tube rupture, according to the SONGS SPAR model, is 4.26E-7/yr”. Subsequent investigations revealed premature wear on the steam generators of both reactors; 17 months later it was decided to decommission both units | PWR | Operational | 1127 | 1983 | Cost but low safety relevance | 0 | Steam generator | 1 | inadequate design control | H | 2500 | 10000
88 | 30 | 1 | 2012 | Byron, United States | United States | Energy | Plant | BYRON | 2 | 2 |  | 1 to 2 | NA | Transformer and breaker failures cause loss of offsite power, reactor trip, and de-energized safety buses. The key issue for this event is the potential for operators to fail to recognize this scenario. | PWR | Operational | 1210 | 1987 |  | 1 |  | 2 |  | T | 15 | 25
89 | 9 | 2 | 2012 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 1 | 0 | 2 | 0 to 1 | A | Station blackout, during cold shutdown state, occurred when workers made a mistake that led to a disconnection of grid power supply, and a standby back up diesel generator failed to start automatically, another generator was out of service for maintenance and a third was available for manual start; reconnection to the grid within 12 min; slight increase of core and used fuel pond temperatures. | PWR | Permanent Shutdown | 607 | 1977 |  | ? |  | 2 |  | H | 0 | 0
91 | 21 | 12 | 2011 | Cattenom, France | France | Energy | Plant | CATTENOM | 2,3 | NA | 2 | 0 to 1 | WE | Absence of a siphon-breaker orifice on the fuel storage pools of the two units during inspection; potential inadvertent operations including extraction of water from the pool. | PWR | Operational | 1362 | 1987;1990 |  | 0 | Fuel storage pool | 1? | Inadequate design | H | 0 | 1
93 | 19 | 10 | 2011 | Karachi, Pakistan | Pakistan | Energy | Plant | KANUPP | 1 | 0 | 1 | 0 to 1 | A | Seven-hour emergency imposed after heavy water leaked from a feeder pipe to the reactor, during routine maintenance shut down; no damage or radiation; plant restart after 4-5 weeks. | PHWR |  | 100 | 1971 |  | ? |  | 1 |  | T | 2 | 5
96 | 23 | 8 | 2011 | Mineral, United States | United States | Energy | Plant | NORTH ANNA | 1,2 | 2 |  | 2 | NA | Reactor automatically shutdown and four back-up diesel generators started, when the plant lost off site power due to a beyond design basis earthquake; coincided with the Unit 1 turbine-driven auxiliary feedwater (AFW) pump being out-of-service because of testing; one EDG suffered a coolant leak and stopped working, but was replaced by a fifth one; off site power was restored on the same day. | PWR | Operational | 990;1011 | 1978;1980 | Beyond design basis earthquake! CCDF should be large? | 1 |  | 3 |  | T | 222 | 272
98 | 7 | 6 | 2011 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | 0 |  | 2 to 3 | NA | The failure of a safety-grade electrical breaker and subsequent fire resulted in a large quantity of soot and smoke and impacted some safety-grade equipment; the resulted in a loss of spent fuel pool cooling function and if the reactor would have been at power, loss of a safety function or failures in systems used to mitigate an event could have occured. | PWR | Permanent Shutdown | 512 | 1973 | Spent fuel pool cooling affected; not reactor itself. | 1 |  | 3 |  | T | 0 | 10
99 |  |  | 2011 | Narora, India | India | Energy | Plant | NARORA | 1 | 2? | 1 | 0 to 1 | A | During refueling operation a pair of spent fuel bundle got detached from its end plates resulting in separation of fuel pins from the fuel bundle. The event occurred due to a mechanical fault in fuel transfer system, used for transferring spent fuel from reactor building to spent fuel storage bay. The fuel pin of the spent fuel bundle got damaged during the fuel transfer operation, as was evident from the minor release of iodine and fission product noble gas through the stack at the time of the event. | PHWR | Operational | 220 | 1989 |  | ? | Fuel transfer system | 1 | mechanical fault | T | 0 | 1
101 | 27 | 4 | 2011 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 1,2,3 | 2 |  | 1 | NA | All three reactors scrammed due to loss of external power caused by a tornado in the vicinity of the plant. Control rod insertion and cooling procedures operated as designed with no physical damage or release of radiation. Emergency diesel generators (EDGs) provided power after a brief period of outage. An Unusual Event, the lowest level of emergency classification, was declared by NRC due to loss of power exceeding 15 minutes. Additionally, a small oil leak was found on one EDG; one EDG of unit 3 was out of service due to maintenance. | BWR | Operational | 1155 | 1973;1974;1976 |  | 1 |  | 3 |  | T | 150 | 250
102 | 25 | 3 | 2011 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 1 | 1 |  | 0 to 1 | NA | Unit experienced a brief partial loss of power, while performing start up activities. Automatic systems restored the power; the operating staff responded according to procedure. | PHWR | Operational | 542 | 1971 | Candu anomaly | 0 |  | 1 |  | T | 1 | 10
105 | 11 | 3 | 2011 | Ohkuma-Machi, Japan | Japan | Energy | Plant | FUKUSHIMA-DAIICHI | 1,2,3,4 | 2 | 7 | 0 to 1 | A | A beyond design 9.0-9.2 seaquake and a 14-14.5m tsunami caused total loss of AC/DC power due to flooding; subsequent loss of core cooling; hydrogen explosions; high release due to deliberate containment venting; 20km exclusion zone; 150'000 people continuously displaced; discharge of radioactive coolant water into the sea; all units given up; excessive clean up. | BWR | Permanent Shutdown | 460;784;784;784 | 1970;1973;1974;1978 |  | 1 |  | 3 |  | T | 257000 | 357000
106 | 11 | 3 | 2011 | Onagawa, Japan | Japan | Energy | Plant | ONAGAWA | 2 | 2 | 2 | 2 | A | Following the Tohoku earthquake, a fire broke out in the turbine building; reactor shutdown and power supply by back up diesel generators, that failed after a certain runtime, but were repaired to cool down the reactor without any damage. | BWR | Operational | 825 | 1994 |  | 1 |  | 3;2 |  | T | 4300 | 5000
109 | 7 | 11 | 2010 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 2 | 2 |  | 0 to 1 | NA | An explosion occurred in second main transformer, resulting in an automatic reactor trip and spilling oil into the Hudson River; no safeguard equipment damaged. | PWR | Operational | 1067 | 1973 |  | 0 |  | 2 |  | T | 35 | 50
115 | 28 | 3 | 2010 | Hartsville, United States | United States | Energy | Plant | ROBINSON | 2 | 1;0 |  | 2 | NA | An electrical feeder cable failure to 4 kV non-vital bus 5 caused an arc flash and fire. Non-isolation from bus 4 due to a failure of the breaker to open resulted in reduced voltage to one of the reactor coolant pumps and in a reactor trip; subsequently an automatic safety injection occured due to reactor cooldown. During plant restoration the crew made mistakes and caused a second fire. | PWR | Operational | 780 | 1970 |  | 1 |  | 2? |  | T | 10 | 50
116 | 28 | 3 | 2010 | Perry, United States | United States | Energy | Plant | PERRY | 1 | 2 |  | 0 to 1 | NA | There was a fire in a lubrication system for one of the water pumps that feeds water for generation of steam. Reactor power automatically lowered to 68% due to the reduction in feed water flow, and the fire was extinguished in less than three hours. | BWR | Operational | 1303 | 1986 | minor safety significance - omit | 0 |  | 2 |  | T | 0 | 5
117 | 16 | 3 | 2010 | Leiston, United Kingdom | United Kingdom | Energy | Plant | SIZEWELL | B | 2 |  | 0 to 1 | WE | The reactor was safely shutdown after a small leak (5 liters/minute) was detected, subsequently traced to the bottom of the pressurizer; due to a fault within one of 78 heater elements, a tube developed cracking such that there was a water path into the containment building. The plant was taken offline for 6 months because of difficult repairs. | PWR | Operational | 1250 | 1995 |  | 0 |  | 1 |  | T | 350 | 500
120 | 1 | 12 | 2009 | Cruas, France | France | Energy | Plant | CRUAS | 4 | 2 | 2 | 1 to 2 | WE | Vegetation in the river Rhone, after heavy rain, blocked the water intake of the cooling system, forcing reactor shutdown, and triggering internal emergency plan; no damage or release. | PWR | Operational | 956 | 1984 |  | 1 |  | 3 |  | T | 1 | 10
121 | 23 | 11 | 2009 | Romney Marsh, United Kingdom | United Kingdom | Energy | Plant | DUNGENESS | B2 | 2 |  | 0 to 1 | WE | A fire occurred in the boiler annexe area and forced the shutdown of the affected reactor. Separately, during significant safety assessment work the licensee identified cables in the boiler anexes of both reactors (21 and 22 (on periodic shutdown)) that were insufficiently protected against hot gas release. | GCR | Operational | 615 | 1985 | minor safety relevance - omit (?). Issue with cables not fully considered in current assessment. | 0 |  | 2 |  | T | 50 | 80
123 | 5 | 11 | 2009 | Pierrelatte, France | France | Energy | Plant | TRICASTIN | 2 | 0 | 1 | 0 to 1 | WE | A fuel assembly got caught on the upper internal structures during discharge operations; evacuation and isolation of the reactor building; under water cooling according to normal shutdown procedures. | PWR | Operational | 955 | 1980 |  | ? | Fuel transfer system | 1 |  | ? | 0 | 10
126 | 27 | 8 | 2009 | Sosnovyy-Bor, Russia | Russia | Energy | Plant | LENINGRAD | 3 | 2 | 0 | 1 to 2 | EE | A crack developed in the discharge accumulator of the reactor's feed pump forced the reactor to be shutdown for extended repairs, restart after one year. | LWGR | Operational | 1000 | 1979 | no significant safety relevance | 0 | Feed pump | 2 |  | ?T | 10 | 400
127 | 19 | 8 | 2009 | Burlington, United States | United States | Energy | Plant | WOLF CREEK | Single | 2 |  | 2 | NA | Complete loss of offsite power to the two essential 4 kV bus transformers for about 49 seconds due to lightning strike on a nearby substation, resulting in a turbine trip and subsequent reactor trip sinc all reactor coolant pumps tripped on under-frequency. | PWR | Operational | 1285 | 1985 |  | 1 |  | 3 |  | T | 10 | 15
129 | 30 | 7 | 2009 | Braidwood, United States | United States | Energy | Plant | BRAIDWOOD | 2 | 2 |  | 1 | NA | After a switching procedure from a system to a unit auxiliary transformer, one reactor coolant pump tripped unexpectedly due to over-current which resulted in a reactor trip and subsequently in a turbine generator trip that caused transformers to become de-energized, which in turn caused remaining three reactor coolant pumps to trip off due to loss of power to their busses. Following this "loss of offsite power situation" emergency diesels were started and loaded the safety related busses and allowed the auxiliary feedwater pumps to be operated. Since some non-safety-related equipment was not available, the operators used a "feed&bleed" mode of pumping water into the steam generator and removing the steam through relief valves to the atmosphere. After more than half a day the reactor coolant pressure was low enough to place the residual heat removal system in the shut down cooling mode. | PWR | Operational | 1230 | 1988 |  | 1 |  | 2 |  | H | 10 | 20
131 | 12 | 7 | 2009 | Forked River, United States | United States | Energy | Plant | OYSTER CREEK | Single | 2 |  | 2 | NA | Loss of offsite power due to a lightning strike and caused short circuits, resulted in opening of generator output breakers, fast closure of turbine control valve and, finally, reactor scram. De-energization of the safety-related 4 kV busses caused a pressure increase of the reactor coolant system (RCS), controlled by opening of electromatic relief valves, followed by initiation of both isolation condensers. The main feed pumps, powered from non-safety-related busses, tripped while both emergency diesel generators started and allowed the operators to start the second control rod drive pump to feed cooling water into the RCS to restore the reactor pressure vessel water level. The short interruption of power for the reactor protection system caused primary and secondary containment isolations, including closure of the main steam isolation valves. Besides unsuccessful attempts to early restore offsite power to all safety-related buses and placing the emergency diesel in a standby status, the response to this event was basically as designed. | BWR | Operational | 652 | 1969 |  | 1 |  | 3 |  | T | 5 | 10
135 | 26 | 3 | 2009 | Daisy, United States | United States | Energy | Plant | SEQUOYAH | 1,2 | 2 |  | 1 | NA | Partial loss of offsite power after loss of Common Station Service Transformer results in dual-unit reactor trips and extended loss of offsite power to a safety bus in each unit; all four emergency diesel generators automatically started and systems functioned as designed; reactor coolant system temperatures were controlled by steam generator atmospheric relief valves. | PWR | Operational | 1221;1200 | 1980;1981 | interesting precursor | 1 |  | 3 |  | T | 10 | 20
137 | 25 | 2 | 2009 | Seabrook, United States | United States | Energy | Plant | SEABROOK | 1 | ? |  | 1 | NA | An inadequate design of the cooling water flange of the emergency diesel generator (EDG) B resulted in a cooling water leak during a routine test and operators secured the affected EDG without completing the test. | PWR | Operational | 1296 | 1990 | minor safety significance | 0 | EDG | 1 | Inadequate design | H | 0 | 1
139 | 3 | 11 | 2008 | Morris, United States | United States | Energy | Plant | DRESDEN | 3 | 0? |  | 1 | NA | Failure to prevent inadvertent, uncontrolled control rod withdrawal by non-licensed operators during maintenance activities. | BWR | Operational | 935 | 1971 | attested low to moderate safety significance (WHITE via SDP evaluation) | ? |  | 1 |  | H | 0 | 0
140 | 2 | 11 | 2008 | Palo, United States | United States | Energy | Plant | DUANE ARNOLD | 1 | 2 |  | 1 | NA | Emergency diesel genenator B output breaker tripping under full load conditions during monthly surveillance test | BWR | Operational | 624 | 1974 | no immediate safety concern attested | 0 | EDG | 1 | Inadequate maintenance | H | 0 | 1
142 | 20 | 9 | 2008 | Bridgman, United States | United States | Energy | Plant | COOK | 1 | 2 |  | 1 | NA | Main turbine and generator were damaged by severe turbine vibrations caused by broken low-pressure turbine blades. Reactor manually tripped and all major safety systems functioned as designed. Fire caused by leaking hydrogen, extinguished after roughly 20 minutes; "unusual event" terminated after about 8 hours. | PWR | Operational | 1131 | 1975 | good example of well controlled event | 0 |  | 2 |  | T | 1250 | 1450
144 | 11 | 9 | 2008 | Monticello, United States | United States | Energy | Plant | MONTICELLO | Single | 2 |  | 1 | NA | A cable fault tripped the transformer which supplied power to the site. This resulted in a loss of off-site power to some plant equipment and other equipment problems in safety-related systems; the plant was automatically shut down. | BWR | Operational | 691 | 1971 |  | ? |  | 2 |  | T | 15 | 25
145 | 28 | 8 | 2008 | Tihange, Belgium | Belgium | Energy | Plant | TIHANGE | 1 |  | 1 | 1 | WE | Maintenance operations revealed that one out of two fans, for the management of air, was not functioning, due to incomplete replacement of the electrical control device; no direct safety relevance. | PWR | Operational | 1009 | 1975 |  | 0 | Containment | 1 | Improper maintenance | H | 0 | 0
146 | 8 | 6 | 2008 | Philippsburg, Germany | Germany | Energy | Plant | PHILIPPSBURG | 1 | 1 | 1 | 1 | WE | Leakage between containment and lining identified by a pressure test at the end of start up process after revision, caused by permutation of circuit points in measuring lines after replacement. | BWR | Permanent Shutdown | 926 | 1979 | impairment of safety function of containment - clearly no significant contribution to CCDP | 0 |  | NA |  | H | 8 | 10
148 | 24 | 6 | 2008 | Daeniken, Switzerland | Switzerland | Energy | Plant | GOESGEN | Single | 1 | 1 |  | WE | On reentry after the 2008 revision deadline, two safety-relevant rectifiers had failed. The plant continued its approach after the disturbance had been rectified, although the cause of the double failure was not known. Thus, it has violated a central principle of safety. In addition, the Gösgen NPP reported the incident to ENSI only in March 2009. | PWR | Operational | 1060 | 1979 | INES 1 according to “non-safety-oriented handling of a multiple failure by the same error mechanism (common mode failure)”. | 1 |  | 1 |  | T | 0 | 1
149 | 4 | 6 | 2008 | Krsko, Slovenia | Slovenia | Energy | Plant | KRSKO | Single | 2 | 0 | 1 | EE | Safe shut down of plant after a primary circuit leak was detected, and coolant spilled into the containment; no damage to the core, no release to the environment; repair within days. | PWR | Operational | 727 | 1981 |  | 1 |  | 1 |  | T | 5 | 10
150 | 4 | 10 | 2008 | Narora, India | India | Energy | Plant | NARORA | 1 | 2 | 1 | 1 | A | One instrumented relief valve (IRV) of the primary heat transport (PHT) system opened spuriously due to the failure of its actuator diaphragm. This resulted in hot PHT coolant entry to bleed condenser (BCD) and automatic reactor trip on 'PHT system pressure very low'. Automatic start of standby pressurizing pump but on observing rise in BCD pressure, operator manually stopped that pump and all the four running primary circulating pumps in contravention of operating procedures. Finally emergency core cooling system (ECCS) injected heavy water as PHT pressure dropped below set point, etc. (see ref. for further mechanisms). Emergency was declared and lifted after normalizing the plant status roughly 4 hours later. | PHWR | Operational | 220 | 1989 | INES 1 due to some design and operational deficiencies - interesting precursor. Human error did not have a strong impact on course of events. | 1 |  | 1 |  | T | 0 | 10
155 | 26 | 2 | 2008 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3,4 | 2 |  | 1 | NA | Both reactors were tripped from 100% power when both channels of the safety-related 4 kV bus undervoltage relays actuated, following a momentary grid voltage disturbance. Concurrently, the unit 4 (non safety-related) C bus de-energized and tripped the 4B steam generator feed pump. Auxiliary feedwater pumps started on both units when the steam generator narrow levels dropped below 10%. Offsite electrical power remained available to implement Emergency Operating Procedures and emergency diesel generators did not auto start because of the short duration of the grid voltage disturbance. Thus, the plant response was as designed with one minor complication, the inadvertent actuation of the auxiliary feedwater system on unit 4. | PWR | Operational | 829 | 1972;1973 | minimal safety significance acc to NRC | ? |  | 2? |  | T | 15 | 19
157 | 21 | 8 | 2007 | Beznau, Switzerland | Switzerland | Energy | Plant | BEZNAU | 1 |  | 1 |  | WE | There was a combined unavailability of emergency diesel generators. | PWR | Operational | 380 | 1969 |  | 1 |  | ? |  | ? | 0 | 0
158 | 28 | 6 | 2007 | Brunsebuttel; Geesthacht, Germany | Germany | Energy | Plant | BRUNSBUETTEL; KRUEMMEL | Single,Single | 2 | 0 | 1 | WE | Short circuit occurred during maintenance work at Brunsbüttel; grid connection failed; disconnected from the grid and manually shut down; fire in the turbine building, cracks detected in pipe coverings. 30 minutes of electricity supply interruptions in the Hamburg area effecting traffic lights and all underground trains. Reconnected to grid on 1 July. Brunsbüttel may have triggered (grid-facilitated trip) short circuit in transformer at Krummel, resulting in burning transformer oil. Fire controlled. Failure of the internal power supply; Reactor manually shut down. Expert inspection found that one of the pumps which supply water to the reactor had shut down unexpectedly, and two safety and relief valves had opened accidentally. The result was that the water level and the pressure in the reactor fell quickly. Balanced by switching on a reserve supply system. Operational data missing ; police investigation for violation of procedure ; intense political criticism of information handling. Restart June 2009. Context: Germany's long-running ideological battle over the planned phasing out of nuclear energy by 2020. After the 2007 accidents in Kruemmel (and Brunsbuettel, which is still off-line) the company lost already some 250,000 customers in Northern-Germany. Following market deregulation and a higher retail churn--coupled with the nuclear outages at two of Vattenfall's German reactors--Vattenfall lost about 250, 000 customers in Germany in 2007. Spent €300 million ($420 million) upgrading the plant post 2007 incident. [a124-a127] [a124, a125, a126] | BWR | Permanent Shutdown | 1402;806 | 1983;1976 |  | 1 |  | 2;3 |  | H? | 2014 | 2405
160 | 18 | 7 | 2007 | Kashiwazaki, Japan | Japan | Energy | Plant | KASHIWAZAKI KARIWA | 1,2,3,4,5,6,7 | 2 | 0 | 3 | A | A 6.6 offshore earthquake, with a shock beyond design/basis, initiated a complete shutdown of the plants (9230 MWe) for 21 months and seismic upgrades; units 1,5,6 were in operation and automatically shutdown; an electric transformer at unit 3 caught fire, which was put out 2 hours later. | BWR | Operational | 1100;1100;1100;1100;1100;1356;1356 | 1985;1990;1992;1993;1989;1996;1996 |  | 1 |  | 3 |  | T | 12600 | 16100
161 |  |  | 2007 | Surat, India | India | Energy | Plant | KAKRAPAR | 2 | 2 | 1 | 1 | A | 240 V AC Class II uninterrupted control power supply got affected and reactor tripped automatically. The cause of the event was attributed to deficient design of electrical system that resulted in common mode failure of control power supply. | PHWR | Operational | 220 | 1995 | Potential CCF | ? |  | 1 |  | T | 0 | 1
165 | 30 | 5 | 2007 | Oldbury-on-Severn, United Kingdom | United Kingdom | Energy | Plant | OLDBURY | A2 | 2 |  | 0 | WE | The power station was shut down as part of standard emergency procedure when at 9:40am a fire broke out on one of the generator transformer HV bushings. No-one was injured in the fire and no radiation was released. Information suggests an insulator overheated, causing it to fail. All emergency procedures were commenced, and by 11:30am the situation was stabilised. The power station resumed production for a few days in June then shut down again. | GCR | Permanent Shutdown | 230 | 1968 | unplanned scram - omit (?) | 0 |  | 2 |  | T | 1 | 20
167 | 7 | 5 | 2007 | Philippsburg, Germany | Germany | Energy | Plant | PHILIPPSBURG | 1 | 1 | 1 | 1 | WE | Identified leakage of the containment during refilling with nitrogen after revision due to false positioning of two valves controling the personal access lock. | BWR | Permanent Shutdown | 926 | 1979 | deviation from technical specification - anomaly, clearly no significant contribution to CCDP | 0 |  | NA |  | H | 0 | 0
168 | 6 | 4 | 2004 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 3 |  |  | 0 | NA | An automatic reactor trip (RT) occurred due to a turbine-generator trip as a result of a fault on the 31 main transformer. All control rods fully inserted and all required safety systems functioned properly. | PWR | Operational | 1085 | 1976 |  | 0 | Power supply: main transformer | 2 | most probable cause: design weakness | ?H | 40 | 60
169 | 6 | 3 | 2007 | Leibstadt, Switzerland | Switzerland | Energy | Plant | LEIBSTADT | Single | 2 | 1 |  | WE | Opening of 8 out of 16 safety blow-off valves due to faulty implementation of instructions. Release of large amounts of steam into the pressure suppression pool lead to decreasing water level in the reactor pressure vessel and automatic reactor scram; plant response largely as designed. | BWR | Operational | 1275 | 1984 | INES 1 because of faulty implementation of procedures (human failure, primary circuit) | 1 |  | 1 |  | H | 5 | 10
173 | 15 | 10 | 2006 | Biblis, Germany | Germany | Energy | Plant | BIBLIS | A,B | 2 | 1 | 0 | WE | Placing of anchor bolts to fix safety relevant systems not according to specifications during backfitting measures at both units. | PWR | Permanent Shutdown | 1225;1300 | 1974;1976 | INES 0, later upgraded to 1 due to deficits in quality mangement - no significant safety relevance attested (human failure, primary circuit) | 0 |  | 1 |  | H | 1500 | 2500
174 | 25 | 7 | 2006 | Oesthammar, Sweden | Sweden | Energy | Plant | FORSMARK | 1,2 | 2 | 2 | 2 | NE | Due to work being inappropriately carried (outside core building) out a short circuit occurred which led to a separation of the plant from the high voltage grid, which in turn caused an unexpectedly high voltage spike and the loss of two of the four trains of the emergency power supply as well as to the loss of houseload power supply. Only two remaining intact supply lines were available for controlling the event. Cooling of the reactor core was always possible because of the 4x50% design of the emergency and safety sytems. The full power supply was re-established after about 22 minutes through manual switching. Approximately 20 minutes after the initial event, the 500 V diesel bus bars in the affected divisions were manually connceted to the 6 kV system, supplied by the off site auxiliary power, and all electrical systems were thereby operational. The scram of the reactor was successful, all control rods were inserted as expected. Two valves in the pressure relief system opened because of unwarranted initiation of safety trains. The emergency core cooling system in two out of four trains was however more than sufficient to maintain the reactor level above the core, as there were no additional LOCA. The control room staff had difficulties in supervising the plant properly during the event as many indications and readings were lost due to the loss of power in two trains. | BWR | Operational | 1022;1158 | 1980;1981 | INES 2 due to degradation of safety systems but with sufficient provision of safety - interesting precursor. Increase to level due to common cause failure in the emergency power supply system (failure of two out of four UPS DC/AC inverters). | 1 |  | 2? |  | H | 400 | 600
175 |  |  | 2006 | Surat, India | India | Energy | Plant | KAKRAPAR | 1 | 2 | 1 | 1 | A | Two of the three instrumented relief valves (IRVs) of the primary heat transport (PHT) system opened inadvertently during unit operation, automatically tripping the reactor on PHT System Low Pressure. The operators closed the IRVs manually. The cause of the event was attributed to earth faults since wrong wiring connections remained unnoticed. There was no external heavy water leak during the event. | PHWR | Operational | 220 | 1992 | Potential CCF | ? |  | 1 |  | T | 0 | 1
177 |  |  | 2006 | Surat, India | India | Energy | Plant | KAKRAPAR | 2 | 2 | 1 | 1 | A | During reactor operation, an auxiliary feed water line (10% flow) to one of the steam generators (SGs) inside the secondary containment of reactor building ruptured. This resulted in loss of water inventory from condensate and feed water system and consequently in low water levels in the SG. | PHWR | Operational | 220 | 1995 |  | ? |  | 2 |  | T | 1 | 10
178 | 20 | 2 | 2006 | Marseilles, United States | United States | Energy | Plant | LASALLE | 1 | 1 |  | 1 | NA | During shutting down for refueling, the plant's turbine control system malfunctioned, finally scraming the reactor; all control rods were inserted within 4 min and all safety system including the ECCS functioned well. | BWR | Operational | 1207 | 1982 | candidate for precursor study | 1 |  | 2 |  | T | 0 | 1
180 | 21 | 12 | 2005 | Avoine, France | France | Energy | Plant | CHINON | B1,B2,B3,B4 | 2 | 1 | 1 | WE | An ill-conceived surveillance of the tertiary cooling water intake canal led to its significant silting up; the collapse of the sand hill could have led to the heat sink loss of all four reactors. | PWR | Operational | 954 | 1982;1983;1986;1987 | potential common cause failure | 1 |  | 3 |  | H | 0 | 10
181 | 30 | 9 | 2005 | Nogent-sur-Seine, France | France | Energy | Plant | NOGENT | 1 | 1 | 1 | 1 | WE | Water escaped pipes feeding the secondary circuit of the reactor by drain valves that were unusually open. The water seeped into the building, leading to insulation faults on electrical equipment of the reactor protection system . These defects caused the automatic shutdown of the reactor and the decommissioning of two of the four sensors which measure the reactor power. | PWR | Operational | 1363 | 1987 |  | 1 |  | 2 |  | T | 1 | 50
184 | 16 | 5 | 2005 | Cattenom, France | France | Energy | Plant | CATTENOM | 2 | 2? | 1 | 2 | WE | Sub-standard of the secondary coolant pump power supply cabling lead to a fire in an electricity funnel; one out of two safety circuits had to be disconnected, triggering local internal emergency plan. | PWR | Operational | 1362 | 1987 |  | 1 |  | 1 or 2? |  | T | 1 | 10
185 | 6 | 3 | 2007 | Leibstadt, Switzerland | Switzerland | Energy | Plant | LEIBSTADT | Single |  | 1 |  | WE | Reaktorschnellabschaltung auf Grund des Öffnens von Sicherheitsabblaseventilen Das der Stufe INES 1 zugeordnete Vorkommnis ereignete sich am 6. März 2007, nachdem durch eine fehlerhafte Vorgehensweise bei der leittechnischen Absicherung für Instandhaltungsarbeiten an Blitzschutzbeschaltungen das automatische Druckentlastungssystem SEHRADS initialisiert wurde. Dies führte zum Öffnen von 8 der 16 Sicherheitsabblaseventile. Dadurch wurde plötzlich eine grosse Menge Frischdampf aus dem Reaktor direkt in die Druckabbaukammer geleitet. Diese zusätzliche Dampfabfuhr aus dem Reaktor führte zu einem raschen Absinken des Füllstandes im Reaktordruckbehälter. Beim Unterschreiten des dafür vorgesehenen Grenzwertes löste der Reaktorschutz auslegungsgemäss die automatische Schnellabschaltung des Reaktors aus. Unmittelbar danach wurden die Frischdampfisolationsventile automatisch geschlossen, die Speisewasserpumpen abgeschaltet und nach etwa zwei Minuten erfolgte die Isolation des Containments. Die Hochdruck-Noteinspeisesysteme RCIC und HPCS wurden gestartet, ebenso die Notstromdieselgeneratoren. Die Schichtmannschaft fokussierte sich in der Anfangsphase auf die Sicherstellung eines genügenden Füllstands im Reaktordruckbehälter. In der zweiten Phase wurde der Druck im Reaktordruckbehälter stabilisiert, gefolgt vom Abkühlen der Anlage. | BWR | Operational | 1275 | 1984 |  | 1 | Refuelling | 1 | Human error | H | 0 | 10
187 | 17 | 4 | 2005 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 3 | 2 |  | 0 | NA | Millstone plant safely shut down without incident when a computer circuit card signaled an unsafe drop in pressure in the reactor's steam system, e.g., due to a steam line break, when in reality there was no drop in steam pressure; the cause was attributed to "tin whiskers". | PWR | Operational | 1280 | 1986 | interesting anomaly; potentially generic | 0 | Instrumentation & Control: solid state protection system (SSPS) | 1 | whisker growth | T | 25 | 40
188 | 7 | 4 | 2005 | Gravelines, France | France | Energy | Plant | GRAVELINES | 3 | 2 | 1 | 1 | WE | During the year 2006 the operator has noticed the presence of provisional pieces of equipment on both of the reactor protection control command lines. These pieces were applied during the previous reactor outage and had been left there by mistake. Under accidental conditions certain automatic sequences would not have taken place in a normal way. | PWR | Operational | 951 | 1980 |  | 1 |  | 1 |  | H | 0 | 0
189 | 1 | 3 | 2006 | Vratza, Bulgaria | Bulgaria | Energy | Plant | KOZLODUY | 5 | 2 | 2 | 2 | EE | Some of the 60 control rods in the reactor appeared not functioning; when operators tried to activate one cluster of control rods to lower reactor capacity by 30%, after one-out-of four main cooling pumps became disconnected; three out of the six rods remained stuck; remaining clusters were tested after run down of the reactor by pumping boric acid, resulting in a total of 22-out-of-60 rods appeared not functioning, maybe due to inadequate testing after safety upgrades. | PWR | Operational | 1000 | 1987 |  | 1 |  | 1 |  | T | 100 | 200
190 | 11 | 2 | 2005 | Carlton, United States | United States | Energy | Plant | KEWAUNEE | Single | 2 |  | 2 | NA | Due to design flaw the safe shutdown of the reactor could have been jeopardized had an internal flooding occurred; rector remained offline for four months while this and other design issures were being addressed. During a past inspection, Nuclear Regulatory Commission inspectors identified, and Kewaunee later reported, that the Kewaunee plant design for internal flooding events may not mitigate the consequences of non-safety related piping system failures in the turbine building. High water level in the turbine building would result in water flowing into certain Engineered Safety Features (ESF) equipment rooms because ESF rooms are separated from the turbine building by non-water-tight doors and the plant floor drain system. The ESF equipment rooms contain the auxiliary feedwater system (AFW), emergency diesel generators, and both 480 volt and 4160 volt ESF switchgear. The water could reach levels that may result in failure of certain ESF and plant safe shutdown equipment. Documentation which considers specific flooding events from postulated failures of plant equipment exists; however, a complete internal plant flooding analysis was not developed during or subsequent to the plant's original design. In response to the inadequate plant design, physical changes were made to minimize challenges to plant equipment and personnel in combating potential flooding events. Although an event resulting in actual flooding of any portion of the plant has not occurred, the potential for certain piping and tank failures resulting in unacceptable flooding existed. The licensee completed a past operability evaluation to assess what equipment would have failed during postulated flooding events. The NRC Significance Determination Process assessed the safety consequences and implications for any equipment that would have failed and determined that the condition was characterized as Yellow (i.e., an issue with substantial importance to safety, that will result in additional NRC inspection and potentially other NRC action). Licensee Event Cause Summary Design basis documentation regarding flooding, high energy line break, seismic, and tornado protection lacked detail and was difficult to retrieve, and some processes related to maintaining the design basis were weak and were inconsistent with industry standards. The plant staff lacked a thorough knowledge of the design basis and fully effective processes for determining the significance of problems and prioritizing their resolution. The plant staff evaluation and resolution of identified and potential problems lacked rigor. The probabilistic risk assessment (PRA) submitted for Kewaunee's individual plant examination (IPE) was flawed with respect to flooding risk. | PWR | Permanent Shutdown | 595 | 1974 |  | 1 |  | 1 |  | T | 120 | 160
192 | 23 | 8 | 2004 | Brunsbuettel, Germany | Germany | Energy | Plant | BRUNSBUETTEL | Single | 2 | 1 | 1 | WE | Turbine and reactor shutdown after a short circuit in a below ground cable of the own station power supply system probably due to aging of the PVC-isolation; switch to offsite power supply as pre-selected. | BWR | Permanent Shutdown | 806 | 1976 | INES 1 due to potential common cause failure mechanism (aging) - clearly no contribution to CCDP | 0 |  | 2 |  | T | 1 | 10
193 | 9 | 8 | 2004 | Mihama, Japan | Japan | Energy | Plant | MIHAMA | 3 | 2 | 1 |  | A | Five workers died, and six workers were injured, due to a leak in a pipe in the turbine hall, that resulted in the release of 270C steam; substantial loss of reactor coolant levels, forcing the plant to immediately shut down. | PWR | Operational | 826 | 1976 | Primarily a mechanical injury event. Safety relevance related to loss of secondary coolant and low water level in one (?) out of three steam generators. | 1 |  | 2 |  | T | 1200 | 2000
194 | 27 | 7 | 2004 | Neckarwestheim, Germany | Germany | Energy | Plant | NECKARWESTHEIM | 2 | 1 | 1 | 1 | WE | Radioactivity entered into the secondary circuit via deionized water system that fed into the steam generator because of a missing check valve. Very minor activity release to the atmosphere. | PWR | Operational | 1400 | 1989 | minor safety relevance - human failure - omit (?) | 0 |  | 1 |  | T | 1 | 10
195 | 14 | 6 | 2004 | Surat, India | India | Energy | Plant | KAKRAPAR | 1 | 0 | 1 | 1 | A | An event of reactor power rise took place during refuelling of a coolant channel. The reactor regulating system rods were not in position to compensate for positive reactivity addition due to refuelling. Operator further raised the reactor demand power, which prevented the addition of boron poison to the reactor. | PHWR | Operational | 220 | 1992 | (known to be sensitive to reactivity-induced incidents) | ? |  | 1 |  | H | 0 | 0
196 | 14 | 6 | 2004 | Wintersburg, United States | United States | Energy | Plant | PALO VERDE | 1,2,3 | 2 |  | 1 to 2 | NA | A ground fault in the electrical grid resulted in losses of offsite power to all three units at Palo Verde. With the exception of one EDG in Unit 2, all EDGs started and loaded onto engineered safeguard buses. | PWR | Operational | 1414 | 1985;1986;1987 |  | 1 |  | 3 |  | T | 40 | 60
197 | 10 | 6 | 2004 | Brunsbuettel, Germany | Germany | Energy | Plant | BRUNSBUETTEL | Single | 2 | 1 | 1 | WE | Deviation of boron concentration in the (nuclear) poisoning system from specification, identified during inspection, active over years of operation. | BWR | Permanent Shutdown | 806 | 1976 | INES 1 due to lack of safety culture - minor degradation of a diverse safety system - omit (?) | 0 | (nuclear) poisoning system | 1 | deficiencies in safety culture | H | 0 | 0
198 |  |  | 2004 | Kaiga, India | India | Energy | Plant | KAIGA | 2 | 2 | 1 | 1 | A | ECCS nitrogen gas accumulator got slightly depressurised during monthly surveillance testing. This accumulator is used for light water injection under pressure to the PHT system during loss of coolant accident. ECCS accumulator remained depressurised for three hours while the unit was operating. This resulted in deviation from technical specifications of the plant. | PHWR | Operational | 220 | 1999 |  | 0 |  | 1 |  | H | 0 | 0
199 |  |  | 2004 | Kota, India | India | Energy | Plant | RAJASTHAN | 2 | 1 | 1 | 1 | A | During unit start up, subsequent to partial loss of class IV power supply failure, reactor was tripped manually. The event was rated at level 1 on INES, as there was a procedural deficiency, which allowed reactor to remain operational under 2 % full power without an automatic trip. | PHWR | Operational | 200 | 1980 |  | 0 |  | 1 |  | H | 0 | 10
200 |  |  | 2004 | Kota, India | India | Energy | Plant | RAJASTHAN | 4 | 2 | 1 | 1 | A | During surveillance testing, one of the redundant valves of the emergency core cooling system (ECCS) was found not operating. It was not possible to rectify the valve during unit operation; since this was not in accordance with technical specifications, the plant management was directed to shutdown the unit and rectify the problem. | PHWR | Operational | 220 | 2000 | Shortage of information about level of redundancy; probably <10^-6 | ? |  | 1 |  | T | 0 | 1
201 | 27 | 5 | 2004 | Leibstadt, Switzerland | Switzerland | Energy | Plant | LEIBSTADT | Single | ? | 1 | 1 | WE | Shutdown of the plant due to increased activity level of the reactor coolant resulting from leakiness of a fuel rod and hence in the air of the drywell. To allow accessibility of the drywell for inspection and repair the ventilation system was switched to operational modes, i.e., exhaust air via activated carbon filter, open isolation flaps between the drywell and containment, only allowed under cold shutdown conditions. During restart these flaps must be switched to closed which was falsely not done and was against technical specifications; slightly increased release of iodine (2% of weekly emission limit). Subsequent analysis revealed that during the switching over of the afterheat removal system to emergency standby mode, 3-4 cubic meters of reactor coolant unexpectedly flowed backward into the pressure suppression pool which contributed to the iodine release. | BWR | Operational | 1275 | 1984 | INES 1 due to violation technical specification - primary, human | ? |  | 1 |  | H | 4 | 7
202 | 28 | 5 | 2004 | Leibstadt, Switzerland | Switzerland | Energy | Plant | LEIBSTADT | Single | ? | 1 | 1 | WE | Stepwise replacement of fuel elements by new designs caused a change of the moderator temperature reactivity coefficient which became finally positive at temperatures below 140 celsius. When making the reactor critical at 50 celcius, the reactor behaved in a way which the operating staff was not experienced and trained, leading to a core heat-up rate above allowed level but did not cause harm to the reactor pressure vessel. | BWR | Operational | 1275 | 1984 | INES 1 due to violation technical specification - primary, human | ? |  | 1 |  | H | 0 | 10
203 | 9 | 5 | 2004 | Biblis, Germany | Germany | Energy | Plant | BIBLIS | B | 2 | 1 | 1 | WE | Deactivation of torque switches of two mounting drives due to hitherto undetected failures of the vendor. | PWR | Permanent Shutdown | 1300 | 1976 | INES 1 due to potential common cause failure mechanism - clearly no safety relevance, omit | 0 |  | ? |  | T | 1 | 5
206 | 9 | 3 | 2004 | Léré, France | France | Energy | Plant | BELLEVILLE | 2 | 2 | 2 |  | WE | Generic anomaly. Insulation faults of electrical cables within the reactor building, which could prevent the operation of safety relevant equipment in some accident conditions. 44 reactors affected. | PWR | Operational | 1363 | 1988 |  | 1 |  | 1 |  | T | 0 | 50
207 | 9 | 3 | 2004 | Penly, France | France | Energy | Plant | PENLY | 2 | 2 | 2 | 2 | WE | An insulation default at an electrical switchboard was triggered by a steam leak close to electrical equipment that was to be qualified to resist accidental conditions; the non-conformity of the cabling has been subsequently identified on all of the French NPPs and led to large-scale verification and remediation operations | PWR | Operational | 1382 | 1992 | potential common cause failure due to non-conformity, with specifications, of cables relevant to primary circuit; | 1 |  | 2 |  | T | 1 | 10
208 | 10 | 3 | 2004 | Surat, India | India | Energy | Plant | KAKRAPAR | 1 | 2 | 2 | 2 | A | Operating at a power level of 70 % full power, an unintended reactor power increase took place. Prior to the event, while carrying out certain maintenance work, power supply to all the adjuster rods of the reactor regulating system failed and the regulating rods became inoperable. Further, operator inhibited the automatic liquid poison addition system to prevent addition of the boron poison to the moderator which could have arrested the reactor power rise. The reactor power rise could not be arrested by the regulating system and reactor tripped at a power level of 98 % full power. The reactor trip settings were corresponding to 90 % full power as against the operating power level of 70% full power. The incident reflected weakness in plant safety culture and highlighted the need to improve safety practices further. | PHWR | Operational | 220 | 1992 |  | 1 |  | 1 |  | T;H | 20 | 30
209 | 16 | 3 | 2004 | Philippsburg, Germany | Germany | Energy | Plant | PHILIPPSBURG | 2 | 2 | 1 | 1 | WE | Deviations from technical specification identified during maintenance for fasteners (pins missing) of pumps of safety-related systems foreseen to transfer horizontal loads from external events such as earthquakes. | PWR | Operational | 1468 | 1984 | insufficient quality assurance | 0 |  | 1 |  | H | 1 | 10
213 | 20 | 8 | 2003 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | 0 |  | 0 | NA | A Slammer worm penetrated a private computer network, although protected by a firewall, and disabled the safety monitoring system for nearly 5 hours; the breach did not pose a safety hazard as the plant has been offline since Feb 2002 and was equipped with a redundant analog backup. | PWR | Operational | 925 | 1977 | incident relates to SCADA issues | 0 | Instrumentation & Control: Safety Parameter Display System | 1 | Inadequate maintenance | H | 0 | 0
216 | 29 | 4 | 2003 | Philippsburg, Germany | Germany | Energy | Plant | PHILIPPSBURG | 1 | 2 | 1 | 1 | WE | Foreign substances (cleaning paper) found during revision of check valves of the fast reactor shudown system in several check valves and some other elements and also in the mechanical part of one control rod drive, left by a contracted company after the 2002 revision. | BWR | Permanent Shutdown | 926 | 1979 | INES 1 due to potential impact on system performance and insufficient quality assurance – Attested: no reactor safety relevance/reactor operated properly for almost one year(?) | 0 |  | 1 |  | H | 0 | 1
217 | 25 | 4 | 2003 | Narora, India | India | Energy | Plant | NARORA | 2 | 0 |  | ? | A | Under annual shut down, during in-service inspection of coolant channel, leak occurred in coolant channel. About six tons of heavy water escaped from primary heat transport system. A plant emergency was declared at 1140 h. The leak was brought under control by various steps taken by the operators and the plant emergency was terminated at 1225 h. The leakage of heavy water from the channel was stopped completely by 2100 h. | PHWR | Operational | 220 | 1992 |  | ? |  | 1 |  | H | 0 | 1
219 | 10 | 4 | 2003 | Paks, Hungary | Hungary | Energy | Plant | PAKS | 2 | 0 | 3 | 3 | EE | Damage of cladding during cleaning of fuel elements; escape of radioactive gas forced workers to escape from reactor hall; minor atmospheric release; capacity reduced, returned to full power after 2005. | PWR | Operational | 500 | 1984 |  | 1 |  | 1 |  | T | 300 | 500
222 | 15 | 1 | 2003 | Bridgman, United States | United States | Energy | Plant | COOK | 1 | 2 |  | NA | NA | A fire in the main transformer resulted in an automatic reactor shutdown; release of cooling oil to lake Michigan. | PWR | Operational | 1131 | 1975 |  | 0 |  | 2 |  | T | 35 | 50
223 | 22 | 11 | 2002 | Tihange, Belgium | Belgium | Energy | Plant | TIHANGE | 2 | 0 | 2 |  | WE | The reactor was in hot shut down mode when a "wrongly scheduled test" caused the pressurizer relief valve to open, so that the primary coolant pressure dropped to about 85 bars, triggering a number of safety systems which started injecting water into the primary system. Due to communication problems it took 3 minutes to get the key action done, i.e. to close the valve and stop the leak. No environmental impact. | PWR | Operational | 1055 | 1982 | degradation of defense-in-depth - human error | 1 |  | 1 |  | H | 0 | 0
227 | 12 | 9 | 2002 | Brunsbuettel, Germany | Germany | Energy | Plant | BRUNSBUETTEL | Single | 2 | 1 | 1 | WE | Further deviations in the control of emergency and decay heat removal system following the analysis of simulator results | BWR | Permanent Shutdown | 806 | 1976 | safety-relevant observations during simulator testing - omit (?), see also events 61 and 56 | 1 |  | 1 |  | T | 0 | 0
228 | 3 | 9 | 2002 | Geesthacht, Germany | Germany | Energy | Plant | KRUEMMEL | Single | 2 |  | 1 | WE | Incomplete opening of various armatures to limit reactor pressure on demand and additional case of loss of preferred power, identified during inspection. | BWR | Permanent Shutdown | 1402 | 1983 | INES 1 due to potential design flaw (CCF) – questionable, if minor CCDP | 1 |  | 1 |  | T | 0 | 0
230 | 27 | 8 | 2002 | Brunsbuettel, Germany | Germany | Energy | Plant | BRUNSBUETTEL | Single | 2 | 1 | 1 | WE | Identification of deviations regarding protective functions in case of loss of preferred power during test of new simulator. | BWR | Permanent Shutdown | 806 | 1976 | safety-relevant observations during simulator testing - omit (?), see also events 53 and 61 | 1 |  | 1 |  | T | 0 | 1
231 | 2 | 8 | 2002 | Neckarwestheim, Germany | Germany | Energy | Plant | NECKARWESTHEIM | 1 | 2 | 1 | 0 | WE | False mounting of burst disc provided to allow for redundant exhaust of annular space between safety vessel and reactor building. | PWR | Permanent Shutdown | 840 | 1976 | limited safety relevance - safety function in case of demand ensured - omit (?) | 0 | Containment: annular space extraction | 1 | Incorrect installation | H | 0 | 0
232 | 5 | 8 | 2002 | Sosnovyy-Bor, Russia | Russia | Energy | Plant | LENINGRAD | 3 | 1 |  | 2 | EE | During major planned repairs at the reactor block, 241 used - and thus practically defective - ball-type flow meters were installed in the reactor instead of new ones. To conceal the fact that these flow meters had already been used, 231 of 241 were put through decontamination and electro-chemical polishing in the chemical service shop. These operations rendered the sensitive devices unsuitable for use. After the repairs, during restart, the defective meters started to fail, resulting in a loss of control over the water flow in the fuel assembly channels, creating preconditions for a nuclear accident. | LWGR | Operational | 1000 | 1979 | significant event - considered as an act of sabotage | 1 |  | 1 |  | H | 7 | 10
233 |  | 8 | 2002 | Dunbar, United Kingdom | United Kingdom | Energy | Plant | TORNESS | 1 | 2 |  | 1 | WE | The sudden and extensive failure of a gas circulator in May 2002 was thought, from forensic evidence, to be linked to the development of an unexpected fatigue related crack in part of the impeller. In August, another gas circulator on the other unit showed signs of increasing vibration and was promptly shut down by the operators. Its subsequent disassembly revealed a fully developed fatigue related crack in a similar position to the first failure, but the prompt shutdown had prevented consequential damage. | GCR | Operational | 682 | 1988 | no acute safety relevance due to large energy storage capacity; aging as CCF | 1 |  | 1 |  | T | 180 | 300
234 | 31 | 7 | 2002 | Philippsburg, Germany | Germany | Energy | Plant | PHILIPPSBURG | 2 | 0 | 1 | 0 | WE | Failure to open of the burst disc of the annular space after spurious start of exhaust ventilator during revision work. | PWR | Operational | 1468 | 1984 | limited safety relevance - safety function in case of demand ensured - omit (?) | 0 |  | 1 |  | T;H | 0 | 0
235 | 17 | 7 | 2002 | Brunsbuettel, Germany | Germany | Energy | Plant | BRUNSBUETTEL | Single | 2 | 1 | 1 | WE | Identification (during test of new simulator) of a design flaw in the control system of the emergency power supply, and emergency and decay heat removal system. | BWR | Permanent Shutdown | 806 | 1976 | safety-relevant observations during simulator testing. In principle a long term vulnerability (since 1979) - see also events 53 and 56 | 1 |  | 1 |  | T | 0 | 10
237 | 5 | 6 | 2002 | Neckarwestheim, Germany | Germany | Energy | Plant | NECKARWESTHEIM | 1 | 0 | 1 | 1 | WE | Faulty handling and positioning of a fuel element during inspection caused by a technical failure in the loading machine and subsequent human error; no loss of leak tightness of the two affected fuel elements. | PWR | Permanent Shutdown | 840 | 1976 | INES 1 due to potential systemic failure and deficits of the maintenance program - no activity release, clearly no reactor safety relevance/no contribution to CCDP - omit | 0 | Fuel transfer system | 1 |  | T;H | 0 | 0
239 | 21 | 5 | 2002 | Philippsburg, Germany | Germany | Energy | Plant | PHILIPPSBURG | 1 | 0 | 1 | 0 | WE | Faulty opening of several power switches in one out of six 0.4 kV emergency power busses during periodic testing causing loss of that train of the emergency power supply system of insignificant safety relevance. | BWR | Permanent Shutdown | 926 | 1979 | INES 1 due to a systematic failure and deficits in the maintenance program - no actual safety relevance - omit (?) | 0 | Power supply: .4 kV emergency power bus | 1 | systematic error and deficiencies in the maintenance program | H | 0 | 0
241 | 11 | 3 | 2002 | Heysham, United Kingdom | United Kingdom | Energy | Plant | HEYSHAM | A1 | 0 |  | 2 | WE | After removal of a new fuel assembly from a buffer store tube, the fuelling machine inserted the short shield plug and was then jacked up. Upon trying to move away fom the standpipe, the machine showed signs of stalling and a bang was heard. Refuelling was immediately suspended and the investigations have since shown that the grab had not disengaged from the short shield plug due to failure of a drive coupling on the grab disengage drive. At the time when the machine had tried to move away, part of the short shield plug became separated and dropped into the buffer store tube. | GCR | Operational | 625 | 1983 | INES 2 due multiple failures of safety provisions | ? | Fuel transfer system | 1 |  | T | 1 | 5
243 | 27 | 2 | 2002 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | 2 |  | 2 | NA | Plant staff discovered that borated coolant water had leaked from a cracked control rod drive mechanism, directly above the reactor, and eaten through the pressure vessel head, leaving only 9.5mm of stainless steel cladding holding back the high pressure (17 MPa) reactor coolant. A breach most likely would have resulted in a massive loss of coolant accident, resulting in a jet that might have damaged adjacent control rod drive mechanisms; the resulting safety reviews, repairs and upgrades took 2 years (upon which they placed a downtime cost of $600 million); the operator first energy was fined $33 million. [s03] | PWR | Operational | 925 | 1977 |  | 1 |  | 1 |  | T | 3000 | 5000
244 | 21 | 1 | 2002 | Flamanville, France | France | Energy | Plant | FLAMANVILLE | 2 | 2 | 2 | 2 | WE | Starting with an error of maintenance workers, while replacing electrical components on one electrical panel; manual restart of the faulty system, finally resulting in a situation where batteries were the only power source left to one of the two instrumentation and control systems; reactor shutdown; failure of the cooling system of primary pump seals and prevention of switch over to backup system; start of an extra backup system and manual restart after its shutdown by overload protective system; restoration of power supply of failed system after some hours, but occurrence of additional equipment failures, and hydrogen leak from the generator; restart on 1/30 after major repair. | PWR | Operational | 1382 | 1986 |  | 1 |  | 1? |  | T | 15 | 18
245 | 14 | 12 | 2001 | Brunsbuettel, Germany | Germany | Energy | Plant | BRUNSBUETTEL | Single | 2? | 1 | 1 | WE | Oxyhydrogen explosion caused damage to a small pipe of an auxiliary system used to cool the reactor pressure vessel head during shutdown; continuous full power operation until early inspection; one year plant shutdown for safety checks and upgrades. | BWR | Permanent Shutdown | 806 | 1976 |  | 1 |  | 1 |  | T | 350 | 600
246 | 20 | 11 | 2001 | Narora, India | India | Energy | Plant | NARORA | 1 | 2 | 1 |  | A | The end-fitting blank for one of the coolant channels (G-17) developed a leak due to larger bore diameter than specified. The reactor was immediately shut down. About 1.4 tonnes of heavy water leaked from the Primary Heat Transport System, mostly recovered using the mopping system available in the plant. Minor exposure of employee, and releases within specified limits. | PHWR | Operational | 220 | 1989 |  | ? |  | 1 |  | T | 1 | 10
247 | 27 | 9 | 2001 | Surat, India | India | Energy | Plant | KAKRAPAR | 1 | 0 |  | ? | A | Under annual shut down, there was an incident of flash over and burning of the power supply cable of one of the process water pumps. This was caused by spurious connection to two independent (redundant) power sources simultaneously caused by faulty control logic. This resulted in complete loss of power to the emergency power supply buses. All the loads connected to these buses, became unavailable. After the source of fire was identified and isolated, the power supplies and the connected loads were restored, in about 1 hour and 15 minutes. During this period of non-availability of power supply, forced circulation of Primary Heat Transport (PHT) and moderator systems were not available. Due to this, the temperature of these systems increased marginally by about 5 Celcius. The reactor had been shut down for about 24 days before this incident. | PHWR | Operational | 220 | 1992 |  | ? | Power supply: for process water pumps | 2 | malfunction in the control logic of circuit breaker | T | 0 | 0
248 | 10 | 8 | 2001 | Philippsburg, Germany | Germany | Energy | Plant | PHILIPPSBURG | 2 | 1 | 2 | 2 | WE | Restart of reactor after refueling with boron concentration below prescribed value in two out of four refilled flooding tanks; unauthorized reactor operation for one month; no danger for the public according to investigations. | PWR | Operational | 1468 | 1984 |  | 1 |  | 1 |  | H | 1 | 10
253 |  | 5 | 2001 | Leiston, United Kingdom | United Kingdom | Energy | Plant | SIZEWELL | B | 2 |  | 1 to 2 | WE | The reactor was shut down to investigate high accumulations of water in the containment, confirmed by analysis to be primary coolant leakage; the leak had been suspected as coming from an instrumentation seal but discovered to have been escaping from the seal between the RPV and its head. The investigations by the licensee led to improvements in Foreign Material Exclusion and actions to take upon discovery of water in the containment. | PWR | Operational | 1250 | 1995 | Interesting candidate for precursor study | 1 |  | 1 |  | T | 30 | 40
255 | 11 | 4 | 2001 | Kuznetsovsk, Ukraine | Ukraine | Energy | Plant | ROVNO | 2,3,4 | 2 | 1 | 2 | EE | During the dismounting of a lifting crane, it fell on the trestle with cables passed from 330/6kV transformers to unit 4 (under construction). Due to the resulting earth fault, outside 300kV transmission lines were cut off by electrical protection actuation lines; there was a loss of normal and emergency power supply leading to decreasing frequency of the power supply of the main coolant pumps and actuation of emergency protection including scramming of units 2 & 3. Because of overload the central alarm indication system was disabled that caused difficulties in the event management by the personel. The earth fault caused high currents, burning of the cables, and the following fire spread to 6 kV distribution buses. The fire was extinguished after 1 1/2 hours; the plant was kept under hot standby condition and restarted after permission. | PWR | Operational | 415;1000;1000 | 1981;1986;2004 | interesting event, also for multiple units at different operational states | 1 |  | 3 |  | H | 10 | 100
256 | 2 | 4 | 2001 | Dampierre-en-Burly, France | France | Energy | Plant | DAMPIERRE | 4 | 0 | 2 | 1 | WE | During reloading, an error in the charging order occured, due to human and organizational faults, which could have led to a criticality risk. | PWR | Operational | 937 | 1981 | Unlikely to contribute to CCDF, however limited information. | ? |  | 1 |  | H | 0 | 1
258 | 18 | 3 | 2001 | Heng Chun, Taiwan, China | Taiwan, China | Energy | Plant | MAANSHAN | 1,2 | 1? |  | 2 | A | Seasonal smog, containing salt deposits, caused malfunction of all four 345 kV transmission lines and loss of offsite power at Maanshan 1; reactor in hot standby condition; both emergency diesel generations failed to operate; auxiliary feedwater system properly operating by turbine driven pump; restoration of essential power supply by successfully connected swing emergency diesel generator after two hours; reactor in safe condition, no radiation release. | PWR | Operational | 951 | 1984;1985 |  | 1 |  | 3 |  | T | 1 | 10
260 | 3 | 1 | 2001 | Surat, India | India | Energy | Plant | KAKRAPAR | 2 | 1 | 1 | 1 | A | During start up, failure of pressure control system of Primary Heat Transport system caused the system to get over-pressurized; this resulted in the opening of the relief valves. | PHWR | Operational | 220 | 1995 | Potential for minor / low level precursor | 1 |  | 1 |  | T | 0 | 1
264 | 18 | 12 | 2000 | Madras, India | India | Energy | Plant | MADRAS | 2 | 2 | 1 | 1 | A | During a routine monthly surveillance test, the Emergency Core Cooling System (ECCS) and the associated logic got spuriously actuated. This caused the closure of the Reactor Building Ventilation dampers. On resetting the ECCS, two out of four dampers did not open automatically due to faulty logic relay. After repair, the dampers were checked to be working normally and the system was normalised. | PHWR | Operational | 220 | 1985 |  | 0 |  | 1 |  | H | 0 | 1
265 | 21 | 11 | 2000 | Narora, India | India | Energy | Plant | NARORA | 2 | 0 | 1 |  | A | The unit was in a shut down condition with Pressurized Heat Transport (PHT) system in a cold and depressurised state. It was noticed that heavy water was leaking from a coolant channel due to a defective seal plug. During this incident, two tonnes of heavy water leaked out of the system. A modified temporary blank was inserted to arrest the leak. | PHWR | Operational | 220 | 1992 |  | ? | Pressurized Heat Transport (PHT) system | 1 | defective seal plug | T | 1 | 5
266 | 16 | 11 | 2000 | Narora, India | India | Energy | Plant | NARORA | 2 | 0 | 1 | 1 | A | After refuelling a coolant channel, the empty fuelling machine during its downward movement hit the bottom shield, and was incapacitated. This could have been a serious incident if the fuelling machine were carrying radioactive spent fuel. The root cause of this incident was a procedural lapse; a safety interlock, which was temporarily made ineffective prior to refuelling for solving another problem, was not normalized. | PHWR | Operational | 220 | 1992 |  | 0 |  | 1 |  | T | 0 | 1
269 | 26 | 7 | 2000 | Kaiga, India | India | Energy | Plant | KAIGA | 2 | 1 | 1 | 1 | A | The technical specifications require that both auxiliary boiler feed pumps (ABFP) should be available during start-up. However, in one instance, the unit was started up when one of the ABFP was under maintenance. This amounted to a violation of technical specifications; the pump was made operable a day after the start-up. | PHWR | Operational | 220 | 1999 | INES 1 due to violation of technical specifications; could be studied as a (below threshold) precursor | 0 |  | 1 |  | H | 0 | 0
271 | 28 | 5 | 2000 | Sosnovyy-Bor, Russia | Russia | Energy | Plant | LENINGRAD | 1 | 1 | 1 | 1 | EE | A sharp drop in coolant flow in a fuel assembly channel, caused by a piece of rubber that had been forgotten during repairs, while bringing the reactor to the minimum controlled power level. The personnel's attempts to restore the flow rate were not successful. The reactor had to be shut down. | LWGR | Operational | 1000 | 1973 |  | 0 |  | 1 |  | H | 0 | 10
272 | 15 | 2 | 2000 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 2 | 2 |  | 1 | NA | Steam generator tube failure resulted in an initial primary-to-secondary leak of reactor coolant with a minor radioactivity release to the environment; manual reactor shutdown and steam generator isolation; during plant cooldown an excessive cooldown rate was inadvertently established, and to restore the coolant level in the pressurizer, borated water was added using the safety injection system. Inspection revealed that the licensee did not perform adequate examination of the (4x3 3000) steam generator tubes during its '97 outage. | PWR | Operational | 1067 | 1973 | potential precursor - lack of safety culture | 1 |  | 1 |  | T | 715 | 816
273 | 27 | 12 | 1999 | Braud St. Louis, France | France | Energy | Plant | BLAYAIS | 1,2,3,4 | 2 | 2 | 2 | WE | An unexpected combination of the tide and high winds partially flooded the site with units 1,2,4 operating and unit 3 shut down for refueling; all units lost their 225 kV power supply and units 2 and 4 also lost their 400kV power supply, leading to automatic shutdown after failure of self supply and triggered start of diesel backup generators; damage to safety related systems; inadequate emergency response: restoration of 400kV power supply after less than 3 hours; no damage to the reactors but the event raised concern about similar threats in other plants in France, and caused upgrades of design rules and protection. | PWR | Operational | 951 | 1981;1982;1983;1983 |  | 1 |  | 3 |  | T | 50 | 200
275 | 12 | 7 | 1999 | Tsuruga, Japan | Japan | Energy | Plant | TSURUGA | 2 | 2 |  | 2 | A | Primary coolant water that leaked (50 tons) from cracks (first 4.4 cm long, second 8 cm long and more) in a pipe of the chemical and control system, made of stainless steel. Highest radiation level, 11,500 times the limit, was measured in a room on the second level basement. The operator believed that metal fatigue, caused by repeated stress, resulted in those cracks. | PWR | Operational | 1160 | 1986 |  | 0 |  | 1 |  | T | 130 | 270
276 | 18 | 6 | 1999 | Shika-machi, Japan | Japan | Energy | Plant | SHIKA | 1 | ? | 2 | 2 | A | During regular inspection 3 out of 89 control rods slipped from their normal positions, which triggered a fission chain reaction, and a state of criticality for about 15 min; due to erroneous manual to test actuator ability to move the control rods; nitrogen gas for inserting control rods during an emergency was not ready; workers eventually managed to insert control rods manually into the core. The operator tried to hide the accident, but when it was revealed it forced a 2 year shutdown while investigations were being carried out. | BWR | Operational | 540 | 1993 |  | 1 |  | 1 |  | ? | 624 | 780
277 | 10 | 6 | 1999 | Pierrelatte, France | France | Energy | Plant | TRICASTIN |  | 2 | 1 | 1 | WE | Polyamide cages, non-qualified for accidental situations, instead of metal cages have been built onto ball bearings of coolant safety injection pumps. First identified at the Tricastin site, the problem turned out to be spread over all of EDF's nuclear power plants. | PWR |  |  |  | INES 1 due to potential common cause failure | 0 |  | 1 |  | H | 1 | 10
282 | 27 | 12 | 1998 | Hunterston, United Kingdom | United Kingdom | Energy | Plant | HUNTERSTON | B1,B2 | 2 | 2 | 2 | WE | Severe weather conditions over a 24 h period progressively disabled all grid supplies to the site. With fourth (final) line lost (0:23) both reactors manually tripped and post trip cooling established automatically. Emergency diesel generators (EDG) placed on standby after grid supplies reinstated two hours later. When all grid supplies were lost for a second time (11:05), many difficulties experienced including non fully reset of the reactor shut down sequencing equipment, manual reconfiguration required for essential electrical system, etc. Finally natural circulation cooling established on R3 at 11:35 and on R4 at 13:05; at 14:05 forced circulation cooling established on both units, supplied via EDG, grid supplies restored shortly after. On-site emergency stood down by 22:02. | GCR | Operational | 644 | 1976;1977 | interesting event for further study | 1 |  | 3 |  | T | 10 | 50
283 | 24 | 6 | 1998 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | 2 | 1 | 1 | NA | Struck by a tornado the plant's switchyard was damaged and access to offsite power was disabled; the reactor was automatically shut down and electricity for safety systems was provided by emergency diesel generators until external power could be restored; no activity release. | PWR | Operational | 925 | 1977 | candidate for precursor study | 1 |  | 3 |  | T | 20 | 50
284 | 6 | 6 | 1998 | Stadland, Germany | Germany | Energy | Plant | UNTERWESER | Single | 2 | 2 | 1 | WE | Manual switching of one out of three main steam bypass stations (Frischdampfumleitstation) caused rapid decline of level in tank for turbine oil supply, subsequent turbine shut down and reactor scram. Investigations identified a clogged oil strainer and non-opening of one main steam blow-off/control valve due to valves in the hydraulic servo line, left closed after a previous plant outage. Plant reaction as designed/safety ensured as remaining redundant safety-related equipment of the main steam cycles were functional. | PWR | Permanent Shutdown | 1410 | 1978 | INES 2 attested due to clear administrative and plant control deficits | 0 |  | 2 |  | T | 0 | 10
286 | 12 | 5 | 1998 | Civaux, France | France | Energy | Plant | CIVAUX | 1 | ?1 | 2 | 2 | WE | The reactor had been stopped for 5 days when 180 mm pipe rupture in an auxiliary cooling circuit occured which stayed in contact with the primary circuit. The leak/cracks, caused by design fault, led to the release of radioactive coolant (steam) into the reactor building; the decay heat removal system remained in operation. Urgent repair effectuated after 5 hours; major redesign and back fit of all reactors of same N4 type. | PWR | Operational | 1561 | 1997 | primary circuit – technical/human(design fault) - no significant safety relevance, potential CCF | 1 |  | 1 |  | T | 2500 | 4000
287 | 17 | 4 | 1998 | Geesthacht, Germany | Germany | Energy | Plant | KRUEMMEL | Single | 2 | 1 | 1 | WE | Detection of a systemic design failure in the reactor safety (control) system, affecting the high pressure injection system, during a simulator exercise. | BWR | Permanent Shutdown | 1402 | 1983 | INES 1 due to long detection time - no actual safety relevance/simulator exercise - omit (?) | ? |  | 1 |  | T | 0 | 0
289 | 9 | 9 | 1997 | Bridgman, United States | United States | Energy | Plant | COOK | 1,2 | 2 |  | 1 | NA | Operator faced problems with ice condenser containment system, and declared both containments inoperable; plant shutdown for 3 years. | PWR | Operational | 1131;1231 | 1975;1978 |  | 0 | Containment | 1 | Design | H | 3540 | 4970
290 | 18 | 8 | 1997 | Biblis, Germany | Germany | Energy | Plant | BIBLIS | B | 2 | 1 | 1 | WE | Failure of two out of four pumps of the auxiliary cooling system, located in the same room, because of flooding following a water leakage from the defective bearing of one pump. | PWR | Permanent Shutdown | 1300 | 1976 | anomaly - minor safety significance attested | 1 | Auxiliary cooling system | 1 | Maintenance ? : bearing damage caused by a protective helmet found in the the impeller of the pump | H? | 0 | 1
294 | 15 | 4 | 1997 | Brunsbuettel, Germany | Germany | Energy | Plant | BRUNSBUETTEL | Single | 2 | 1 | 0 | WE | Review of diagrams identified an interlock of the feed-in armature that may affect the functionality control of the core flooding system and was regarded as deviation from specification. | BWR | Permanent Shutdown | 806 | 1976 | INES 1- insufficient safety signifcance attested - omit (?). Design issue. | 0 |  | 1 |  | T | 0 | 0
297 | 20 | 9 | 1996 | Marseilles, United States | United States | Energy | Plant | LASALLE | 1,2 | 2 |  | 1 | NA | Service water system showed declining performance trends spanning two years; event raised doubts whether it could fulfill its safety mission; both units shut down for 2 years to fix the problem, no direct reactor safety relevance. | BWR | Operational | 1207 | 1982;1984 |  | ? |  | 1 |  | T | 2550 | 3130
298 | 5 | 9 | 1996 | Hart Township, United States | United States | Energy | Plant | CLINTON | 1 | 2 |  | 2 | NA | Degradation of a seal and one of the reactor recirculation pumps failed, causing the reactor to be shut down; plant was ready to be restarted by August when electrical breaks failed and demonstrated inadequate preventive measures; shut down for nearly two years. | BWR | Operational | 1098 | 1987 |  | 1 |  | 1 |  | T | 1300 | 1800
299 | 2 | 9 | 1996 | Crystal River, United States | United States | Energy | Plant | CRYSTAL RIVER | 3 | 2 |  | 1 | NA | Innocuous balance-of-plant equipment problem mushroomed when inspections identified other equipment problems stemming from same process flaws; shutdown for all of 1997; no direct reactor safety relevance. | PWR | Permanent Shutdown | 890 | 1977 |  | ? | Multiple systems | 1;2 | Design | H | 1185.75 | 1367.75
304 | 19 | 4 | 1996 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 1,2,3,4,5,6,7,8 | 2 |  | 1 | NA | All eight reactors at the Pickering nuclear stations were shut down to repair a backup valve on the Emergency Core Cooling System. The flaw was detected on April 15th, and the system had been tested one month earlier. Hydro did not advise the public of this situation until April 20th. | PHWR | Operational;Permanent Shutdown;Permanent Shutdown;Operational;Operational;Operational;Operational;Operational | 542;542;542;542;540;540;540;540 | 1971;1971;1972;1973;1982;1983;1984;1986 | unknown if flaw existed before test one month earlier. CCF | 1 |  | 1 |  | T | 50 | 70
307 | 19 | 2 | 1996 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 6 | 2 |  | 2 | NA | About 500 tonnes of water spilled into the reactor building when employees working on an Emergency Water Supply valve failed to isolate it from the system. An investigation revealed that safety equipment could have failed due to water damage, and both the primary and backup heat sinks were actually lost for a section of the reactor core. The accident blew a 60 lb. valve component 6 feet into the air, almost hitting a worker and shot water up to the reactor building dome. | PHWR | Operational | 540 | 1983 | Interesting precursor | 1 |  | 1 |  | H | 1 | 10
310 | 21 | 7 | 1995 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 5 | 2 |  | 1 | NA | Two technicians carried out work on the wrong reactor (reactor 5 instead of reactor 6), disabling the second fast shutdown system on reactor 5, which was operating at full power at the time. | PHWR | Operational | 540 | 1982 | Time period of degraded safety system unknown. Interesting potentially significant maintenance error | 1 |  | 1 |  | H | 0 | 50
311 | 15 | 5 | 1996 | Morris, United States | United States | Energy | Plant | DRESDEN | 3 | 2 |  | 2 | NA | Plunging water levels around the nuclear fuel in the core prompted a shut down of the reactor after inadequate, non-timely handling of sealing problems with one and snapping shut of the second feedwater valve; high pressured safety systems kicked in; restart about 8 months later. | BWR | Operational | 935 | 1971 |  | 1 |  | 1 |  | T | 1 | 5
312 | 20 | 2 | 1996 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 1,2,3 | 2 |  | 2 | NA | Manual shutdown following discovery of a potential common-mode failure that could disable both trains of high-pressure safety injection system, i.e. throttle valves could become clogged with debris; extended outage until mid May, 1999 due to resolution of numerous deficiencies. | BWR;PWR;PWR | Permanent Shutdown;Operational;Operational | 684;918;1280 | 1970;1975;1986 | CCF | 1 |  | 1 |  | T | 3000 | 4000
313 | 30 | 1 | 1996 | Burlington, United States | United States | Energy | Plant | WOLF CREEK | Single | 2 | 2 | 2 | NA | Operators manually tripped the plant from 80% power after frazil ice blocked intake travelling screens and trash racks, and hindered water intake on the circulating service water intake systems; emergency service water system was started but misaligned and the standby circulating water train was put in service; the blockage was removed by sparging with air. | PWR | Operational | 1285 | 1985 | candidate for precursor study | 1 |  | 3 |  | T | 1 | 10
315 | 16 | 5 | 1995 | Salem, United States | United States | Energy | Plant | SALEM | 1,2 | 2 |  | 1 | NA | After manual shutdown ventilation supply system fans for the electrical switchgear room were declared inoperable; restart by April, 1998, after resolution of numerous deficiencies and replacement of steam generator tubes. | PWR | Operational | 1254;1200 | 1976;1981 |  | ? |  | ? |  | T | 2800 | 4000
317 | 14 | 1 | 1995 | Wiscasset, United States | United States | Energy | Plant | MAINE YANKEE | Single | 2 |  | 1 | NA | Steam generator tubes with crack indications were identified during forced outage and needed to be repaired; restart about one year later. On Dec 6 1996 operators manually shut down the unit after multiple safety systems found to be degraded. Plant closed. | PWR | Permanent Shutdown | 900 | 1972 |  | ? | Steam generator | 2 |  | T | 540 | 700
318 | 10 | 12 | 1994 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 2,4 | 2 |  | 3 | NA | A pipe break resulted in a spill of 185 tons of heavy water; this loss of coolant accident was controlled by the Emergency Core Cooling Systems; no major release; restart by mid February, 1996, after clean-up and repair. | PHWR | Permanent Shutdown;Operational | 542 | 1971;1973 |  | 1 |  | 1 |  | T | 500 | 800
319 | 14 | 11 | 1994 | Geesthacht, Germany | Germany | Energy | Plant | KRUEMMEL | Single | 2 | 0 | 1 | WE | Interchange of feedback signals following switching at feed-in switches of double-supplied 380 V emergency power supply buses that remained undetected between two revisions. | BWR | Permanent Shutdown | 1402 | 1983 | INES 1 due lack of detection for more than 3 weeks - omit (?) | ? |  | 1 |  | T | 0 | 0
324 | 29 | 1 | 1994 | St. Vulbas, France | France | Energy | Plant | BUGEY | 5 | 0 | 2 | 2 | WE | The reactor was shut down and the primary coolant level was decreased to working level in order to carry out some maintenance operations; the water flow level at primary pumps and the motor intensity fluctuated for eight hours without any operator intervention, although the technical specifications explicitly require close supervision, because fluctuations can indicate the degradation of the primary pumps leading to their potential loss and thus the risk of core degradation. The safety authorities identified human significant malfunctioning (the manual was erroneous, the operators had not received any specific training) while the situation has been considered falsely as normal and safe, the visit of the safety engineer in the control room did not lead to any corrective action. | PWR | Operational | 917 | 1979 | INES 2 due to safety culture issues. Potential precursor | 1 |  | 1 |  | H | 0 | 0
326 | 25 | 12 | 1993 | Lagoona Beach, United States | United States | Energy | Plant | FERMI | 2 | 2 |  | 1 | NA | Main turbine experienced catastrophic failure after a history of vibrations and little refurbishment during refueling outages; automatic turbine and reactor trip; large fire caused by hydrogen gas for generator cooling; flooding of radioactive waste building by water from affected water piping; restart after 1.1 years of repair/replacement and other measures. [a137] | BWR | Operational | 1198 | 1986 |  | ? |  | 2 |  | T | 830 | 990
327 | 23 | 10 | 1993 | Braidwood, United States | United States | Energy | Plant | BRAIDWOOD | 1 | 2 |  | 1 | NA | Primary-to-secondary coolant leak due to crack in a steam generator tube; reactor had to shut down when ingress rates exceeded acceptable level; a 3.3 centimeter long crack in a single tube located above the top tube support plate near an anti-vibration bar was identified during inspection. | PWR | Operational | 1270 | 1987 | Minor case of classic precursor | 1 |  | 1 |  | T | 1 | 10
328 | 7 | 10 | 1993 | Zarechnyy, Russia | Russia | Energy | Plant | BELOYARSK | 3 | 2 | 1 | 2 | EE | Leak in the primary coolant system of the BN-600 fast breeder reactor resulted in the release of radioactive sodium (into plant); reactor shutdown and evacuation of personnel; the latter necessary because of potential fire/explosion; restart after repair. | FBR | Operational | 600 | 1980 |  | 1 |  | 1 |  | T | 1 | 10
329 | 8 | 9 | 1993 | Biblis, Germany | Germany | Energy | Plant | BIBLIS | B | 2 | 1 | 1 | WE | Rupture of conical valve in one 3-way-valve, forming part of the emergency core cooling system, which switches from water feed-in to recirculation mode in the case of a LOCA. Due to mechanical damage (probably detected during maintenance) this switching function could have failed, reducing degree of redundancy. | PWR | Permanent Shutdown | 1300 | 1976 |  | ? |  | 1 |  | T | 0 | 1
333 | 31 | 3 | 1993 | Narora, India | India | Energy | Plant | NARORA | 1 | 2 | 3 | 3 | A | Major fire in the turbine building, initiated by failure of two steam turbine blades, resulting in severe imbalance in the turbo-generator, and rupturing of hydrogen seals and lube-oil lines; widespread damage to control and power cables, causing loss of indications and loss of power to essential equipment for over 17 hours; manual activation of shutdown system and initiating of fast cool down; decay heat removal by fire water injection into the steam generator; no radiological impact but severe degradation of engineered safety systems. [a137] | PHWR | Operational | 220 | 1989 |  | 1 |  | 2 |  | T | 200 | 500
334 | 25 | 3 | 1993 | Grohnde, Germany | Germany | Energy | Plant | GROHNDE | Single | 2 | 1 | 1 | WE | Irregular installation (mix up) of electronic devices within safety control and communication system, detected by quality assurance program. | PWR | Operational | 1430 | 1984 | INES 1 because the mistake was not detected by previous tests and measures - insignificant safety relevance - omit (?) | 0 |  | 1 |  | H | 0 | 1
335 | 14 | 3 | 1993 | Wintersburg, United States | United States | Energy | Plant | PALO VERDE | 2 | 2 |  | 1 | NA | A tube in the no. 2 steam generator ruptured causing a primary-to-secondary leak of approx. 900 liters per minute; the operators failed twice to diagnose and mitigate the event because the radiation monitors were not in an alarm status (the correct mode for operation) and did not isolate the affected steam generator until almost 3 hours. | PWR | Operational | 1414 | 1986 |  | 1 |  | 1 |  | T;H | 1 | 10
337 | 2 | 3 | 1993 | Daisy, United States | United States | Energy | Plant | SEQUOYAH | 1,2 | 2 |  | 1 | NA | Unit 2 was operating at 100 percent power when a worker attached a fuse-pulling device to the fuse for the feedwater regulating valve’s trip solenoid. This apparently caused the valve to close, causing a pressure transient. A 10-inch-diameter extraction steam pipe ruptured, allowing steam to envelop an electronics cabinet in the area, which in turn caused a reactor trip signal based on false indications of generator voltage problems. Voluntarily shut down of both units to inspect all piping sections of unit 1, as found broken a day before on unit 2; additional cracking found; repair and resolution of other equipment problems, restart of unit 2 late '93, unit 1 spring '94. | PWR | Operational | 1221;1200 | 1980;1981 |  | ? | Extraction steam pipe | 2? |  | T;H | 1200 | 2000
338 | 27 | 2 | 1993 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 3 | 2 |  | 1 | NA | Voluntarily shutdown of to address problems with the anticipated transient without scram mitigation system actuation circuity (AMSAC); identified deficiencies and design errors, extended restart to 2.3 years. | PWR | Operational | 1085 | 1976 |  | 1 |  | 1 |  | T | 900 | 1500
340 | 3 | 2 | 1993 | Bay City, United States | United States | Energy | Plant | SOUTH TEXAS | 1,2 | 2 |  | 0 | NA | Turbine driven auxiliary feedwater pumps failed when tested, placing the unit in limiting conditions for operation; manual reactor shut down; list of items to be completed prior to restart 1.1 years later. | PWR | Operational | 1354 | 1988;1989 |  | ? |  | 1? |  | T | 1600 | 2500
346 | 10 | 9 | 1992 | Neckarwestheim, Germany | Germany | Energy | Plant | NECKARWESTHEIM | 1 | 2 | 1 | 1 | WE | Inaccurate signals of the reactor protection and control system due to coupling of electromagnetic impulses into one train of the redundant system of high safety relevance, during search for earth connections. Reduction of reactor power and temporary shut down of the plant for inspections. | PWR | Permanent Shutdown | 840 | 1976 | INES 1 due to inadequate test procedure (?) - no significant contributiion to CCDP as three redandant trains of the affected system remained operable | ? |  | 1 |  | H | 0 | 10
349 | 28 | 6 | 1992 | Barseback, Sweden | Sweden | Energy | Plant | BARSEBACK | 2 | 1 | 2 | 2 | NE | During restart after revision, leaking water from the primary cooling circuit carried mineral wool away from neighbouring pipes; filters of the emergency pumps were clogged causing failure of the related system for a few hours; no core damage due to low decay heat. | BWR | Permanent Shutdown | 615 | 1977 | High cost due to industry impact; downtime and backfits. | 1 |  | 1 |  | T | 650 | 2000
351 | 13 | 5 | 1992 | Boisar, India | India | Energy | Plant | TARAPUR | 1 |  |  | 3 | A | Sudden drop in reactor power and pressure and emergency consenser shell side water level went off scale; emergency condenser loop A was isolated and generation improved, and all parameters got normalised. Unit operation was continued with emergency condenser loop A isolated; due to the incident, minor radioactivity got released through the emergency condenser vent. Down for two months. | BWR | Operational | 160 | 1969 |  | 1 |  | 1 |  | T | 13 | 17
352 | 21 | 4 | 1992 | Southport, United States | United States | Energy | Plant | BRUNSWICK | 1,2 | 2 |  | 0 | NA | Irregularities in the construction of the building housing the emergency diesel generators during special inspection; voluntary shutdown of both units; restart unit 1 after 1.8 years / unit 2 after 1.1 years, due to detailed inspection of structural components and major upgrades. | BWR | Operational | 990;960 | 1976;1975 | Construction/fabrication issue | ? | structural defects in the EDG building | 3? | systematic problems | H | 1340 | 1580
353 | 24 | 3 | 1992 | Sosnovyy-Bor, Russia | Russia | Energy | Plant | LENINGRAD | 3 | 2 | 2 | 3 or 4 | EE | During refueling, a loss of pressure in one of the pressure seals affected the respective fuel channel; release of radioactive gas including I-131 via filters (?) above or below permissible value; reactor stoppage and cool down. | LWGR | Operational | 1000 | 1979 |  | ? |  | 1 |  | T | 1 | 100
357 | 17 | 11 | 1991 | Oswego, United States | United States | Energy | Plant | FITZPATRICK | Single | 2 |  | 1 | NA | Voluntarily shut down, to comply with terms in its operating license, e.g. assured closing of isolation valves of the core spray system; extended outage to fix problems with fire protection and containment isolation valves, and management deficiencies, ended by Jan '93. | BWR | Operational | 849 | 1975 | Further information needed. | ? |  | 1 |  | T | 637.5 | 737.5
358 | 23 | 9 | 1991 | St. Vulbas, France | France | Energy | Plant | BUGEY | 3 | 3 | 2 | 2 | WE | A leak was identified during the decennial primary circuit pressure test on the support of the control rod drive mechanisms that was going through the reactor vessel head. | PWR | Operational | 945 | 1978 | candidate for precursor study | 1 |  | 1 |  | T | 2000 | 4000
362 | 3 | 4 | 1991 | New Hill, United States | United States | Energy | Plant | HARRIS | 1 | 2 |  | 1 | NA | Discovered damaged piping and valves within the alternate minimum flow system, provided for the pumps in the emergency core cooling system; restart after repair. | PWR | Operational | 960 | 1987 |  | 1 |  | 1 |  | T | 0 | 10
363 | 11 | 3 | 1991 | Brunsbuettel, Germany | Germany | Energy | Plant | BRUNSBUETTEL | Single | 2? | 1 | 1 | WE | Failure of a feedback signal regarding the position of a penetration valve of the intermediate cooling system due to damaged control cable; manually closing of the affected valve. | BWR | Permanent Shutdown | 806 | 1976 | INES 1 ? - no acute safety relevance - omit (?) | ? |  | 1 |  | T | 0 | 0
365 | 9 | 2 | 1991 | Mihama, Japan | Japan | Energy | Plant | MIHAMA | 2 | 2 | 3 | 3 | A | Leakage of about 55 tons of primary coolant, into the secondary coolant loop, due to breaking off of a tube in a steam generator; reactor automatically shut down and cooled by the emergency core cooling system; release of steam from the main relief valve, with small amounts of radioactive noble gas and iodine, 2.3x10^10 and 3.4x10^8 Bq. respectively. | PWR | Permanent Shutdown | 500 | 1972 |  | 1 |  | 1 |  | T | 1000 | 2000
367 | 16 | 1 | 1991 | Geesthacht, Germany | Germany | Energy | Plant | KRUEMMEL | Single | 2? |  | 1 | WE | Non-closure of a penetration valve of an intermediate cooling system; isolation of the penetration by closing of the second (redundant). | BWR | Permanent Shutdown | 1402 | 1983 | INES 1 ? - no acute safety relevance - omit (?) | ? |  | 1 |  | T | 0 | 0
370 | 30 | 10 | 1990 | Cruas, France | France | Energy | Plant | CRUAS | 4 | 2 | 1 | 1 | WE | The explosion of a 6.6 kV commutator caused a fire that entailed the loss of one of the two electrical safety circuits; the destruction of the commutator was caused by the degradation of elastic washers due to the exposure to heat - subsequently, the second line was found to be affected in the same way. | PWR | Operational | 956 | 1984 | Potential CCF | ? |  | 2 |  | T | 1 | 10
371 | 25 | 9 | 1990 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 2 | 2 |  | 2 | NA | “Severe flux tilt", with large power shifts in the reactor core, caused in part by the CANDU-specific design. Staff spent two days trying to stabilize the reactor core before shutting it down, and were later criticized by the authority (AECB) for not shutting it down immediately. | PHWR | Permanent Shutdown | 542 | 1971 | further physical information desirable to assess risk of severe transient | ? |  | 1 |  | H | 0 | 10
373 | 20 | 3 | 1990 | Waynesboro, United States | United States | Energy | Plant | VOGTLE | 1,2 | 2 |  | 2 | NA | At about 9:20 a.m., a truck backed into a support column for the feeder line in the low voltage switchyard, suppying power to one the reserve auxiliary transformers (RAT), each of unit 1 and 2, resulting in a pertinent loss of power. The associated unit 2 emergency diesel generator (EDG) started and loaded the deenergized vital bus. However due to another electrical fault the turbine and reactor were tripped - without any complication. Both (crosstied) vital buses of unit 1 were deenergized an the available EDG startet but shut down automatically after 1.5 minutes; loss of all vital ac power for more than 15 minutes with subsequent shut down of operating reactor heat removal pump, while the standby pump could not be started. Reactor system coolant heat-up, core cooling was reestablished at 11:03 a.m. | PWR | Operational | 1229 | 1987;1989 | Interesting event for further study showing complex behavior of dual crosstied plants at different plant states; potential for lessons for PSA | 1 |  | 3 |  | H | 1 | 10
375 | 24 | 11 | 1989 | Greifswald, Germany | Germany | Energy | Plant | GREIFSWALD | 5 | 2 |  | 3 | WE | Projected shut-off of three main coolant pumps to test automatic reactor shutdown under tilt conditions which failed to function; another pump failed causing overheating 10 to 30 fuel elements before reactor was shutdown manually after 40 to 50 seconds; no core melt, no radioactivity released; permanent plant shut down (after national reunion) due to major safety deficits. | PWR | Permanent Shutdown | 440 | 1989 | Precursor CCDF>10-4/demand | 1 |  | 1 |  | T | 650 | 8600
376 | 19 | 10 | 1989 | Vandellos, Spain | Spain | Energy | Plant | VANDELLOS | 1 | 2 | 3 | 3 | WE | A fire at one of its turbines impaired important nuclear safety functions (challenges to core cooling), and due to economic/political reasons unit had to permanently shutdown; no damage/release [a137] | GCR | Permanent Shutdown | 500 | 1972 |  | 1 |  | 2 |  | T | 600 | 3900
377 | 9 | 10 | 1989 | Haddam Neck, United States | United States | Energy | Plant | HADDAM NECK | Single | 2 |  | 2 | NA | 480 fuel rods were slightly damaged during the operating cycle, by metal chips present in the coolant system after repairing of the thermal shield during preceding outage without maintaining cleanliness standards and imposing restrictions. | PWR | Permanent Shutdown | 603 | 1967 | Not a precursor | 0 |  | 1 |  | H | 0 | 10
379 | 16 | 8 | 1989 | Gravelines, France | France | Energy | Plant | GRAVELINES | 1 | 2 | 3 | 3 | WE | The mounting of an inappropriate type of screws onto pressure relief valves on the primary circuit would have rendered the overpressure protection system inefficient - the valves would have opened and closed significantly later than under design basis conditions. | PWR | Operational | 951 | 1980 | candidate for precursor study | 1 |  | 1 |  | H | 0 | 0
380 | 17 | 3 | 1989 | Lusby, United States | United States | Energy | Plant | CALVERT CLIFFS | 1,2 | 1 |  | 1 | NA | Unit 1 shutdown to inspect pressurized heater sleeves for cracks, after such cracks were discovered on unit 2 during refueling outage; repair of sleeves, and management changes, caused outage extension of 1.4 (unit 1) and 2.1 years (unit 2). | PWR | Operational | 918;911 | 1975;1976 |  | 0 | Pressurizer | 1 | stress corrosion; safety culture | T;H | 1500 | 2500
381 | 5 | 3 | 1989 | Wintersburg, United States | United States | Energy | Plant | PALO VERDE | 1 | 2 |  | 1 | NA | Automatic reactor trip from full power operation due to a false signal from the core protection calculator; ahead of schedule outage lasted 1,3 years to resolve a series of problems, ignored before, and replacement/repair of pressurized relief valves. | PWR | Operational | 1414 | 1985 |  | ? |  | 1 |  | T | 600 | 1000
382 | 7 | 3 | 1989 | Cornelius, United States | United States | Energy | Plant | MCGUIRE | 1 | 2 |  | 1 | NA | 1,900 liters leak per minute (?) developed in steam generator (SG) B caused by IGSCC on the outside diameter of the effected tube. Operators implemented tube leakage procedure and initiated a manual reactor trip 8 to 9 minutes later, began to isolate the SG and initiated reactor cool down and depressurization. By 17 hours (? what was initial time, or was this the duration ?), both trains of the residual heat removal system were in service. Degassing of the secondary circuit led to a release of radioactivity well within the limits of the technical specifications. | PWR | Operational | 1215 | 1981 |  | 1 |  | 1 |  | T | 1 | 10
384 | 22 | 11 | 1988 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 1 | 1 |  | 3 | NA | Power excursion, due to operator error while raising power to avoid a shutdown, following Xenon buildup, caused damage to 36 out of 191 fuel rods, and contamination of the primary cooling system by radioactive iodine. | PHWR | Operational | 542 | 1971 | Precursor. CDF>10^-4. Beyond design basis conditions for ECCS? | 1 |  | 1 |  | H | 1 | 10
385 | 19 | 10 | 1988 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 3 | 2 |  | 1 | NA | A primary-to-secondary leak increased rapidly to 7.6 liters per minute in 2 hours, 7 times greater than the technical specification limit; radition monitoring equipment and leak rate monitoring procedures showed deficits. | PWR | Operational | 1085 | 1976 | INES 1 due to deficit in configuration of (safety relevant) monitoring equipment | 0 |  | 1 |  | T | 1 | 10
386 | 10 | 9 | 1988 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 2 | 1 |  | 1 | NA | Transient induced automatic trip while shutting the reactor down for refueling outage; outage extended to one year due to discovery of pipe wall thickness thinning at fast rate and replacement of many sections, as well as fixing problems with motor-operated valves, emergency diesel generators and control room ventilation system. | PWR | Operational | 890 | 1973 | Lack of official information | ? | Main feedwater pump, refueling cavity floor seal, EDG, control room envelope ventilation system | 1,2 |  | T;H | 421 | 511
387 | 18 | 6 | 1988 | Tihange, Belgium | Belgium | Energy | Plant | TIHANGE | 1 | 2 |  | 2 | WE | A sudden leak occurred in a short, un-isolatable section of the emergency core cooling system piping, which is connected to the hot leg of loop 1 of the reactor core cooling system, while the reactor was operating; notification by the operator after increases in radioactivity and moisture in the containment, and decrease of water level in the volume control tank. | PWR | Operational | 1009 | 1975 |  | 1 |  | 1 |  | T | 0 | 0
388 | 25 | 3 | 1988 | Limerick, United States | United States | Energy | Plant | LIMERICK | 1 | 2 |  | 0 | NA | The reactor was operated over several months with copper concentrations in the reactor coolant at twice the recommended limit, weakening the fuel rod barrier metal. Subsequent fuel rod failures caused reactor power to be limited to 50 percent for the remaining six months of the fuel cycle. | BWR | Operational | 1194 | 1985 | Not a precursor | 0 |  | 1 |  | H | 160 | 210
389 | 19 | 12 | 1987 | Scriba, United States | United States | Energy | Plant | NINE MILE POINT | 1 |  |  | ? | NA | Manual reactor shut down in response to feedwater flow fluctuations caused by vibrating piping; failing to renew license due to numerous problems, e.g., with the core spray system; in summer '89 regulator found excess water dumped into the radioactive waste building, and dozens of drums spilling the highly radioactive contents; restart after 2.6 years. | BWR | Operational | 642 | 1969 |  | ? | core spray system, feedwater system piping | 1,2 |  | H | 1250 | 1600
390 | 16 | 12 | 1987 | Biblis, Germany | Germany | Energy | Plant | BIBLIS | A | 1 | 1 | 1 | WE | Operator did not notice failure-to-close of one out of two valves of an emergency core cooling pipe during reactor restart; second follow up shift tried to deblock valve by missusing a parallel valve of a check line not designed for high operating pressure; opening of relief valve and release of radioactive steam into a room at the containment; closure of valve of check line. | PWR | Permanent Shutdown | 1225 | 1974 |  | ? |  | 1 |  | H | 1 | 10
391 | 15 | 7 | 1987 | Mineral, United States | United States | Energy | Plant | NORTH ANNA | 1 | 2 |  | 1 | NA | A tube of the steam generator C ruptured and led to primary-to-secondary circuit leak; it resulted from high cycle fatigue and the licensee was not fully aware of leakage experienced prior to the rupture. | PWR | Operational | 990 | 1978 | INES 1 due to deficit in safety culture (imprudent operation) | 0 |  | 1 |  | H | 1 | 10
394 | 31 | 3 | 1987 | York County, United States | United States | Energy | Plant | PEACH BOTTOM | 2,3 |  |  | 1 | NA | Recurring equipment problems, frequency of forced outages and operators sleeping on the job (along with other management problems) forced shutdown finally of both units until Dec 89. | BWR | Operational | 1412 | 1974 |  | ? |  | ? | declining performance | H | 2500 | 3500
395 | 9 | 12 | 1986 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 2 | 2 |  | 3 | NA | Catastrophic failure of a suction line of a feed water pump during full power operation, triggered by a main steam line valve failing closed and subsequent pressure increase; reactor fast shutdown and cool down; the steam released by the rupture, caused by severe pipe corrosion and disabled check valve, damaged equipment and resulted in 8 workers injuries, four died later; the event cascaded from the non-nuclear-part across safety-grade systems causing accident management problems. | PWR | Operational | 890 | 1973 | INES 3 omitting fatalities. | 1 |  | 1 |  | T | 75 | 96
397 | 26 | 4 | 1986 | Pripyat, USSR_Ukraine | USSR_Ukraine | Energy | Plant | CHERNOBYL | 4 | 2 | 7 |  | EE | Flawed reactor design and mishandled reactor safety test caused power excursion and steam explosion that destroyed reactor (no containment dome), followed by uncontrollable graphite burning, and meltdown of the remaining core; large release of fuel and radioactive substances; 31 workers/firemen died shortly, several further deaths later; more than 350'000 people evacuated and resettled; 100'000 sq-km contaminated; 4'000 people estimated to die from radiation; loss of site; new shelter under construction. | LWGR | Permanent Shutdown | 1000 | 1983 | Design problematic. | 1 |  | 1 |  | T/H | 578336 | 768336
398 | 11 | 4 | 1986 | Plymouth, United States | United States | Energy | Plant | PILGRIM | 1 |  |  | ? | NA | Recurring equipment problems led to outage; early restarts but shutdowns due to problems with instrumentation, dry well vacuum breakers, and instrument air system; outage extended to 3.2 years due to replacement of main transformer. | BWR | Operational | 711 | 1972 |  | ? | RHR, main transformer, … | 1,2 | declining performance | T;H | 1610 | 1910
402 | 26 | 12 | 1985 | Sacramento, United States | United States | Energy | Plant | RANCHO SECO | 1 | 2 |  | 3 | NA | Following the loss of integrated control system (ICS), unit tripped and an overcooling transient occurred. Plant responded as designed; the auxiliary feedwater (AFW) ICS flow control valves, as well as other valves, went to the 50-percent open position. The auxiliary feedwater flow was excessive. When the local manual attempt to close the flow control valve to the "A" once-through steam generator (OTSG) was unsuccessful, the operator attempted to close the manual isolation valve. This isolation valve could not be moved, even when a valve wrench was used due to lack of any maintenance on valve during life of the plant. Restoration of power within 26 min. Fixing of design flaws and weaknesses during 2.3 years outage. | PWR | Permanent Shutdown | 917 | 1974 |  | 1 |  | ? |  | ? | 700 | 1500
403 | 18 | 12 | 1985 | Forked River, United States | United States | Energy | Plant | OYSTER CREEK | Single | 2 |  | 1 to 2 | NA | Power was increased too rapidly causing both excessive flux peaks and excessive local power increase rates; computer program data, relied upon to guide power increases, was inappropriately based on previous fuel cycle operating data; fuel rod failures resulted in increased levels of gaseous activity; no release. | BWR | Operational | 652 | 1969 | Precursor. 2 relevant safety systems. Inoperability per demand implies CDF 10^-4 for ATWS after failure of automated shutdown system, failure of operator to manually scram the reactor or to start the boron injection system plus emergency core cooling/SG feed systems beyond design specifications. Potential CCF if code used elsewhere. | 1 |  | 1 |  | H | 0 | 0
405 | 14 | 6 | 1985 | Lima, Argentina | Argentina | Energy | Plant | ATUCHA | 1 | 2 |  | 2 | SA | Operators asked to increase power of plant operating in a load following mode; control rod motion resulted in high power peaking and 46 fuel rods to fail, releasing fuel pellets into the reactor coolant system, after misinterpretation of indications and continued reactor operation; no release, restart after about two months. | PHWR | Operational | 362 | 1974 | Potential blockage of flow. | 1 |  | 1 |  | H | 25 | 35
406 | 9 | 6 | 1985 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | 2 |  | 3 | NA | Loss of feedwater. The reactor tripped with MainFeedwater (MFW) Pump 1 tripped and MFW Pump 2 was unavailable. Operators made an error in initiating the steam and feedwater rupture control system and isolated auxiliary feedwater (AFW) to both steam generators(SGs). The PORV actuated three times and did not reseat at the proper RCS pressure. Operators closed the PORV block valves, recovered AFW locally, and used High-Pressure Injection (HPI) Pump to reduce RCSpressure. Provoked investigations where inspectors revealed that maintenance had discovered cracks in the reactor coolant pump shafts; restart 1,5 years later after repair. | PWR | Operational | 925 | 1977 | Major precursor. CCDF 1x10-. | 1 |  | 1 |  | T/H | 871 | 1006
409 | 19 | 12 | 1984 | Forked River, United States | United States | Energy | Plant | OYSTER CREEK | Single | 1 |  | 2 | NA | Control rods were withdrawn to increase power. Local power exceeded prescribed limits when the on-line core monitoring system, not properly programmed and tested, underestimated peaking power. Gaseous activity subsequently increased. Post-shutdown inspection found fuel damaged in 44 assemblies. | BWR | Operational | 652 | 1969 | Precursor (INES 1), requiring physical modeling of reactor. Improper programming and testing as potential CCF. | 1 |  | 1 |  | H | 0 | 0
410 | 15 | 9 | 1984 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 1,2,3 | 2 |  | 1 | NA | Deficiencies caused by programmatic weaknesses, unqualified personal, non-compliance with fire protection regulations; operation suspended of all three units for resolution of programmatic weaknesses; unit 2 down until 1990 (5 yrs), unit 3 until 1994 (10 yrs), and unit 1 until 2006 (20 yrs). Both units at Sequoyah also shut down. Restart of unit 2 early 88 after independent evaluations and repairs, unit 1 followed late 88. | BWR | Operational | 1155 | 1973;1974;1976 |  | ? |  | ? | programmatic weaknesse | H | 8800 | 10200
412 | 23 | 6 | 1984 | Platteville, United States | United States | Energy | Plant | FORT ST. VRAIN | Single | 1 |  | 2 | NA | Recurring problems with moisture intrusion into the primary helium circuit caused failure of 6 out of 37 control rod pairs to insert upon high pressure scram signal at low power level; outage extended to 1.8 years as tests revealed damage of the reserve shutdown system. | HTGR | Permanent Shutdown | 342 | 1976 |  | 1 |  | 1 |  | T | 100 | 300
413 | 16 | 5 | 1984 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | 1 |  | 1 | NA | A tube rupture occurred during plant startup after a refueling outage, while the reactor coolant system was being pressurized for a leak test. It took the operators more than 32 minutes to recognize that a tube rupture had occurred in the B steam generator, and about 40 minutes to isolate the affected steam generator and begin a cooldown of the reactor coolant system. The operator actions after about 40 minutes were effective, however. The leak resulted in a primary system depressurization with no release of radioactivity into the environment. The reactor coolant system remained above the defective steam generator secondary pressure during most of the transient and the defective steam generator overfilled. | PWR | Permanent Shutdown | 512 | 1973 | improper early operator response - no major safety significance, similar to other SG tube leak events | 1 |  | 1 |  | T;H | 1 | 10
414 | 19 | 3 | 1985 | York County, United States | United States | Energy | Plant | PEACH BOTTOM | 2 | 2 |  | NA | NA | (IGSCC) Scheduled outage to replace recirculation system piping; outage extension to 1,2 years as other equipment problems surfaced. | BWR | Operational | 1412 | 1974 |  | 0 |  | 1 |  | T | 500 | 900
415 | 14 | 4 | 1984 | St. Vulbas, France | France | Energy | Plant | BUGEY | 1 or 2 or 3 or 4 or 5 | 2 |  | 3 | WE | Defect in the design of electrical cables linked to the control command center led to a failure led to a failure blacking out unit; reactor shutdown and power supply by emergency diesels; plant operation continued until 1994. | GCR/PWR |  |  |  |  | 1 |  | 1 |  | T | 1 | 10
416 | 10 | 12 | 1983 | Plymouth, United States | United States | Energy | Plant | PILGRIM | 1 | 2 |  | NA | NA | (IGSCC) Plant shut down for planned 10 month outage to replace cracked recirculation system piping; restart after 1.1 years. | BWR | Operational | 711 | 1972 |  | ? |  | 1 |  | T | 300 | 600
419 | 26 | 9 | 1983 | Pope, United States | United States | Energy | Plant | ANO | 1 | 2 |  | 2 | NA | Realignment of a control rod, misaligned for 12 days, at full power operation resulted in xenon oscillations, increasing high local power peaking and damaging the fuel leading to increasing gaseous activity. | PWR | Operational | 903 | 1974 | Similar to E#403 | 1 |  | 1 |  | H | 0 | 0
421 | 7 | 9 | 1983 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 3 | 2 |  | 1 | NA | (IGSCC) During mandated inspection, serious cracking was found in the recirculation system piping; replacement of affected sections slowed by concurrent problems affecting all three units; restart Nov. 1984 | BWR | Operational | 1155 | 1976 |  | 1 |  | 1 |  | T | 600 | 900
422 | 1 | 8 | 1983 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 1,2 | 2 |  | 1 | NA | A two meter-long split of a pressure tube as a result of the mislocation of annulus gas spacer springs; small loca; local fuel damage and safe reactor shutdown by the operators with no increase in radioactive emissions; restart after about 5 years. | PHWR | Operational;Permanent Shutdown | 542;542 | 1971;1971 | The pressure tube failure was a result of unexpectedly high levels of deuterium in the Zircaloy-2 bulk metal, and contact between the pressure tube and calandria tube for a period of seven to ten years | 0 |  | 1 |  | T | 3320 | 5070
423 | 9 | 3 | 1983 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 1 |  |  | 1 | NA | Fuel rods were discovered damaged due to metal chips that had been left in the reactor coolant system after replacement of steam generators without necessary standards of cleanliness; removal of contamination over 5 years of operation. | PWR | Operational | 890 | 1972 | Not a precursor | 0 |  | 1 |  | H | 10 | 100
424 | 26 | 2 | 1983 | Fort Pierce, United States | United States | Energy | Plant | St. LUCIE | 1 | 2 |  | 1 | NA | Workers discovered damaged thermal shield and core barrel support inside the reactor vessel during refueling outage; removal and repair required a 13 month shutdown. | PWR | Operational | 1045 | 1976 |  | ? |  | 1 |  | T | 600 | 800
425 | 15 | 10 | 1982 | Metsamor, USSR_Armenia | USSR_Armenia | Energy | Plant | ARMENIAN | 1 | ? |  | 3 | EE | Switching of reserve service water (boron) pump to vital 6 kW bus ordered during maintenance of any ordinary service water pump; several attempts to start pump after initial failure, followed by a short circuit in the terminal block leading to overheating of cables and finally to a fire in cable compartments and ignition of a bunch of control cables in the main control room 1, resulting in numerous failures in the operation system; all control rods dropped, emergency protection system activated, turbines stopped and generators disconnected from the grid, loss of service transformer due to cable ignition and loss of all main circulation pumps and of vital reliable power supply buses; activation and switching off of two diesel-generators due to short circuit or by the protection system; manual steam dumping by manual operation of the reelief system, core cooling by natural convection; spontaneous short-term operation of feed water pumps and a series of malfunctions and short circuits led to a total plant blackout almost three hours later; more than 5 hours later one of the high pressure injection pumps became operational and 6 ½ hours later all fires were liquidated and the feedwater injection pump was activated, necessary to fill the steam generators and provide primary circuit cooling. Analysis of the emergency shutdown and core cooling showed that the reactor was sufficiently cooled; radiochemical analysis did not reveal damage of fuel elements; after recisions of rules for the design of emergency electric supply (physical and functional separation) and pertinent repairs the plant was restarted in Sept. 1982, and permanently shutdown in 2/1989.[a137] | PWR | Permanent Shutdown | 408 | 1976 | serious precursor/forerunner. Opaque official descriptions. Lessons from Browns Ferry not learned. Questionable operating conditions in Armenia. | 1 |  | 2 |  | H;T | 150 | 250
426 | 9 | 9 | 1982 | Pripyat, USSR_Ukraine | USSR_Ukraine | Energy | Plant | CHERNOBYL | 1 |  | 5 | 5 | EE | Rupture of one of 1640 pressure pipes at 9.6m from the top, due to insufficient flow of coolant; nearby graphite blocks were washed out by water/steam, fuel was sucked into the rupture hole; contamination of reactor building and release of radioactive aerosols through ventilation stock; plant was restarted after repair | LWGR | Permanent Shutdown | 800 | 1977 |  | 1 |  | 1 |  | T | 10 | 100
427 | 28 | 6 | 1982 | Oconee, United States | United States | Energy | Plant | OCONEE | 2 | 2 |  | 1 | NA | While operating at 95% power, a 4-square-foot rupture occurred in a small diameter elbow in a feedwater heat extraction line. The reactor was manually tripped, a steam jet destroyed a non-safety-related load center and certain non-safety-related instrumentation; personnel were hospitalized overnight with steam burns. | PWR | Operational | 891 | 1973 | no significant safety relevance - technical, secondary - omit (?) | 0 |  | 2 |  | T | 1 | 10
429 | 25 | 3 | 1982 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 3 | 2 |  | 2 | NA | Small steam generator tube leak allowed (radioactive) primary coolant water into the secondary circuit; water found leaking through steam generator shell onto the containment floor due to cracks in the girth weld area; repair works and damage to the main generator after first restart forced plant down for about 1.2 years. | PWR | Operational | 1085 | 1976 |  | 1 |  | 1 |  | T | 500 | 700
430 | 20 | 3 | 1982 | Scriba, United States | United States | Energy | Plant | NINE MILE POINT | 1 | 2 |  | 2 | NA | (IGSCC) Plant was shut down after cracks were found in two sections of the reactor's twenty-eight-inch diameter recirculation piping; piping replaced; returned to service in 6/1983. | BWR | Operational | 642 | 1969 |  | 1 |  | 1 |  | T | 510 | 600
432 | 25 | 1 | 1982 | Ontario, United States | United States | Energy | Plant | GINNA | Single | 2 |  | 1 | NA | A 2,900 liters per minute leak developed in steam generator (SG) B caused by foreign parts that fell onto the tubesheet outside the periphery of the tube bundle during earlier modification works. The operators began a power reduction at 1.5 minutes, at 3 minutes the reactor was automatically shutdown and all three safety injection pumps and followed by start of the auxiliary feed pumps started after main feed water isolation; at 5 minutes all the main steam dump valves were in closed condition and the initial reactor coolant system depressurization stopped. At 15 minutes the defective steam generator was isolated and plant cooldown was continuing by natural circulation in loop A and dumping steam from SG A to the main condenser during the first two hours. Following a set of highly complicated actions and system responses including steam relief from SG A to atmosphere; at roughly 21 1/2 hours the residual heat removal system was placed in operation. Minor release of radioactivity. | PWR | Operational | 608 | 1969 | of potential interest for precursor study | 1 |  | 1 |  | T | 80 | 150
434 | 20 | 9 | 1981 | Baxley, United States | United States | Energy | Plant | HATCH | 1 | 2 |  | 2 | NA | Large amounts of cold feedwater were added to the reactor vessel, causing a power transient controlled by insertion of control rods; the utilized geometry resulted in increased power peaking and fuel failures resulting in air ejector activity to rise to 0.3 Ci per second. | BWR | Operational | 911 | 1974 |  | 1 |  | 1 |  | H | 0 | 5
436 | 11 | 2 | 1981 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3,4 | 2 |  | 1 | NA | Voluntarily shut down after futile steps taken to limit steam generator tube degradation rate; replacement of all six steam generators, unit 3 down 210 days (in 1981), unit 4 down 183 days (in 1982) | PWR | Operational | 829 | 1972;1973 |  | 0 | Steam generator | 1 | tube degradation | T | 820 | 910
442 | 13 | 3 | 1980 | Saint-Laurent-des-Eaux, France | France | Energy | Plant | ST. LAURENT | A2 | 2 | 4 | 4 | WE | A malfunctioning cooling system fused fuel elements together at the reactor and ruined the fuel assembly that forced an extended shutdown for 2.5 years. [a93] | GCR | Permanent Shutdown | 530 | 1971 | Precursor beyond design conditions (CCDF ~10^-2) | 1 |  | 1 |  | T | 500 | 1000
446 | 25 | 6 | 1979 | Doel, Belgium | Belgium | Energy | Plant | DOEL | 2 | 1 |  | 1 | WE | A 510 liters per minute leak developed in steam generator B, due excessive residual stresses caused by ovalization of the tubing during fabrication. Despite operator efforts to control the primary system pressure and pressurizer level, automatic high pressure safety injection began at about 19 minutes and caused the pressurizer to become filled with water. The auxiliary feedwater flow to both steam generators automatically started at 41 minutes and then the flow to the defective steam generator was stopped 9 minutes later. The residual heat removal system began operation at 3 1/4 hours. The operators were generally successful in keeping a sufficiently high degree of subcooling in the primary system by shutting down the loop B main coolant pump (a source of heat) and controlling the pressure. No release. | PWR | Operational | 454 | 1975 | of potential interest for precursor study | 1 |  | 1 |  | T | 1 | 10
447 | 28 | 3 | 1979 | Dauphin, United States | United States | Energy | Plant | THREE MILE ISLAND | 2 | 2 | 5 | 5 | NA | Failure in the secondary circuit; reactor scram followed pressure increase in the primary system; a relief valve opened but stuck falsely open; without adequate information from the staff, finally the reactor was starved of coolant, resulting in a severe meltdown and troublesome phenomena; some radioactive gas released, no injuries or adverse health effects, loss of plant; cleanup from 1980 to 1993. | PWR | Permanent Shutdown | 959 | 1978 |  | 1 |  | 2 |  | T/H | 98000 | 190000
449 | 4 | 2 | 1979 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 1,2 | 2 |  | 1 | NA | Voluntarily shut down to replace tube bundles in steam generators after degradation had been evident for at least four years; restart by August '80 with three repaired steam generators. | PWR | Operational | 890 | 1972;1973 |  | 0 |  | 1 |  | T | 1280 | 1510
451 | 31 | 12 | 1978 | Zarechnyy, USSR_Russia | USSR_Russia | Energy | Plant | BELOYARSK | 2 | 2 | 4 | 3 | EE | A short circuit caused a fire in the shared turbine hall, causing collapse of the roof, and damaging oil storage tanks; the intensified fire destroyed measuring lines and cables; subsequent loss of coolant supply and reactor control; fire extinction a few hours later; avoidance of meltdown of reactor cores, overexposure of 8 workers when establishing emergency cooling. [a137] | LWGR | Permanent Shutdown | 160 | 1967 |  | 1 |  | 2 |  | T | 5 | 20
455 | 13 | 12 | 1977 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 1 | 2 |  | 1 | NA | Hydrogen gas explosion damaged three buildings and forced shutdown of reactor. | BWR | Permanent Shutdown | 684 | 1970 | the second explosion was the result of the loss of the seals which occirred in the first explosion but which had not been adequately refilled. | 1 |  | 2 or 3? |  | T/H | 1 | 10
456 | 24 | 9 | 1977 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | 2 |  | 3 | NA | Reactor shut down because of a disruption in the feedwater system; this caused a pressure increase in the primary circuit and the opening of the pilot-operated relief valve (PORV) for the pressurizer which falsely stuck open. | PWR | Operational | 925 | 1977 | forerunner to TMI accident one year later | 1 |  | 1 |  | T | 1 | 10
458 | 15 | 7 | 1977 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 3 | 1 |  | 1 | NA | Startup sequence was begun and over the following 2-day period, problems developed in the off-gas stream filtering system, the concentration of hydrogen became greater than its combustible limit. Various attempts were made to stabilize the system, but they were unsuccessful. The temperature of the charcoal beds and the vault increased throughout the second day, and finally the air stream was diverted from the vault to a bypass system. A stream of nitrogen was passed through the vault to cool the charcoal and to extinguish a fire if one were present. Subsequent examination revealed that a blocked drain in the air system had prevented the air stream from being preheated prior to entering the recombiner. As a result, the catalyst in the recombiner had become ineffective, and a high concentration of hydrogen passed downstream to the vault; it apparently exploded there and ignited the charcoal beds. The purging of the vault by nitrogen had extinguished the fire. There were no injuries, and there was no release of radioactivity. | BWR | Operational | 1155 | 1976 |  | 0 |  | 3 |  | T | 1 | 10
462 | 22 | 2 | 1977 | Jaslovske Bohunice, Czechoslovakia | Czechoslovakia | Energy | Plant | BOHUNICE | A1 | 21 | 4 | 4 | EE | Insufficiently transmissive fuel assembly charged into the reactor one; local overheating caused loss of barriers' integrity between heavy water moderator and fuel with coolant gas (CO2); cladding and steam generator tube corrosion resulted in contamination of the primary and secondary circuit, and of the reactor hall; no significant health impact; reactor decommissioned. | HWGCR | Permanent Shutdown | 143 | 1972 | Major precursor. | 1 |  | 1 |  | T | 2000 | 3000
463 | 13 | 1 | 1977 | Gundremmingen, Germany | Germany | Energy | Plant | GUNDREMMINGEN | A | 2 |  | 1 to 2 | WE | A short circuit, subsequently in both the 220kV lines because of extreme weather, triggered turbine throttling to own power supply level which failed due to falsly adjusted control and opening of gate valves; resulting pressure drop in the primary circuit was interpreted as a large leak followed by an automatic start of the emergency core cooling system; the resulting presssure increase was controlled by opening of relief valves and about 400 cubic meters of hot coolant water were released into the reactor building; the amount of radioactive water was increased by the foreseen operation of the reactor spray system; the radioactive water and radioactive gases were later released to the enviroment in a controlled manner; the costs of repair including decontamination of the reactor building were regarded too high and the plant was permenantly shutdown. | BWR | Permanent Shutdown | 250 | 1966 | a nice example of low safety significance but high costs | 0 |  | 3 |  | T;H | 290 | 4320
464 |  |  | 1977 | Zarechnyy, USSR_Russia | USSR_Russia | Energy | Plant | BELOYARSK | 2 |  | 5 | 5 | EE | Half of the fuel rods melted, releasing fission products; operators exposed; repairs took more than a year. | LWGR | Permanent Shutdown | 160 | 1967 | Insufficient information. Apparent precursor. | 1 |  | ? |  | ? | 600 | 1000
466 | 15 | 9 | 1976 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 2 | 2 |  | 1 | NA | The plant operated at full power with a satisfactory leak rate of 5.3 liters/min when it suddenly developed into rupture of 1250 liters/min, caused by high stress that resulted from the deformation (corrosion) of support plates. After initial measures including control rod manipulations based on misperception, the operators acted promptly and effectively: at 10 minutes they tripped the turbine which caused an automatic reactor shutdown, started the safety injection system and throttled the injection flow to limit reactor coolant system pressure to 14 MPa. At roughly 18 minutes the operators secured feedwater flow to three intact steam generators and isolated the defective one. At 11 hours 20 minutes the plant reached cold shutdown and isolation of the affected loop A. Minimal release of radioactivity. | PWR | Operational | 890 | 1973 | Operator intended to continue operation, against procedure. | 1 |  | 1 |  | T;H | 60 | 100
468 |  |  | 1976 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 1 | 0 |  | 1 | NA | During a shutdown-margin test in the midst of a normal refueling the operator made a failure in rod withdrawal; the reactor went critical but was shut down immediately and automatically. | BWR | Permanent Shutdown | 684 | 1970 |  | 0 |  | 1 |  | H | 0 | 0
469 | 7 | 1 | 1976 | Brownville, United States | United States | Energy | Plant | COOPER | Single | 2 |  | ? | NA | Ice plug formed inside top of off-gas stack, producing a back-pressure permitting release of hydrogen in the off-gas building; hydrogen explosion demolished building; reactor immediately shut down; some release of radioactivity in the vicinity of the explosion; off-gas building was rebuilt, reactor started 11 days later. | BWR | Operational | 801 | 1974 |  | 2 | Event at auxiliary building: explosion at auxiliary off-gas building | 3 |  | T | 10 | 100
470 | 5 | 1 | 1976 | Jaslovske Bohunice, Czechoslovakia | Czechoslovakia | Energy | Plant | BOHUNICE | A1 | 21 |  | 3 | EE | Fresh fuel assembly, together with a technological plug, was ejected into the reactor hall after failure of the closing mechanism of a technological channel during fuel loading; CO2 coolant was flowing out until the refueling machine was reconnected; two workers were suffocated by the CO2; no atmospheric release. | HWGCR | Permanent Shutdown | 143 | 1972 |  | 1 |  | 1 |  | T | 12 | 50
471 | 7 | 12 | 1975 | Greifswald, East Germany | East Germany | Energy | Plant | GREIFSWALD | 1 | 2 | 3 | 3 | EE | Negligent electrical error caused short circuit at transformer, which triggered cable fire with loss of control and power supply of 5 out of 6 main coolant pumps; provisional restoration of power supply; no core damage/release; returned to operation after repair. | PWR | Permanent Shutdown | 440 | 1973 |  | 1 |  | 2 |  | H | 1 | 10
472 | 30 | 11 | 1975 | Sosnovyy-Bor, USSR_Russia | USSR_Russia | Energy | Plant | LENINGRAD | 1 | 2 | 4 | 4 | EE | A fuel channel in Unit 1 suffered a loss of coolant, resulting in the degradation of a nuclear fuel assembly that led to a significant release of radiation lasting for one month; no notification of danger in the affected region. (Chernobyl forerunner) | LWGR | Operational | 1000 | 1973 |  | 1 |  | 1 |  | T | 20 | 100
474 | 5 | 11 | 1975 | Brownville, United States | United States | Energy | Plant | COOPER | Single | 2 |  | 0 | NA | Hydrogen gas explosion at a sump in an auxiliary building; after lifting the manhole cover, two workers physically injured; controlled reactor shutdown; only some radioactivity release in the vicinity of the explosion; restart after short repair. | BWR | Operational | 801 | 1974 |  | 0 | Event at auxiliary building: explosion | 3 |  | H | 1 | 10
475 |  | 5 | 1975 | Hartsville, United States | United States | Energy | Plant | ROBINSON | 2 | 2 |  | 2 | NA | Seal failure in Main Coolant Pump. At full power, an alarm due to leakage from first-stage seal of primary coolant pump, operators started a controlled shutdown, later shutting off the pump. Shortly thereafter the reactor scrammed automatically on a signal from one of the steam generators. Circulation of coolant water to the seals of the remaining primary coolant pumps was blocked, so operator restarted the first pump which operated for about 2 hr, but then the remaining seals collapsed, and primary coolant water began to spill into the containment building at a high rate. Circulation of water through the primary system was maintained by auxiliary means until cold shutdown was achieved and the leak in the primary pump was plugged. By this time about 135,000 gal of primary water had escaped, covering the floor of the containment building to about a foot in depth. Escape of radioactivity to the atmosphere was contained within prescribed limits by the filtering system for the containment building. | PWR | Operational | 780 | 1970 |  | 1 |  | 1 |  | T | 1 | 50
476 | 22 | 3 | 1975 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 1 | 2 |  | 3 | NA | Fire started when a worker, using a candle to search for air leaks, ignited a combustible seal; fire spread on the reactor building side wall, burning for seven hours and damaging cables, disabling systems related to the control of unit 1 and 2; meltdown was averted; all units refurbished and in operation until shutdown in 1985. | BWR | Operational | 1155 | 1973 |  | 1 |  | 2 |  | H | 32340 | 53900
477 | 26 | 2 | 1975 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1 | 2 |  | 1 | NA | A 470 liters/minute leak developed in a steam generator due to tube rupture; operators recognized a leak but thought it was in the auxiliary building. Finally charging pumps were started to control the pressurizer level; load reduction began at 30 minutes and the plant was manually tripped at 47 minutes from 25 % power and the safety injection pumps were intermittently used to control the reactor coolant system inventory. At roughly 3 hours the residual heat removal system was placed in operation; minor realease of radioactivity. | PWR | Operational | 640 | 1970 |  | 0 |  | 1 |  | T;H | 1 | 20
478 | 31 | 10 | 1974 | Morris, United States | United States | Energy | Plant | DRESDEN | 3 | 2 |  | 2 | NA | Control rods operated to achieve better burnup of the fuel in the core bottom, not in line with guidelines; start of a xenon transient causing power peaking, areal clad perforation and minor release of radioactivity; replacement of a number of fuel elements required. | BWR | Operational | 935 | 1971 | Minor precursor. Worse than Oyster Creek 1985. | 1 |  | 1 |  | H | 1 | 10
479 |  | 8 | 1974 | Mihama, Japan | Japan | Energy | Plant | MIHAMA | 1 | 2 |  | 1 to 2 | A | Leak of steam generator tubes occurred (again) and additional wall thinning was revealed; since then, the reactor was stopped for a long period. | PWR | Permanent Shutdown | 340 | 1970 | Further information desirable to assess plant response and severity. | 1 |  | 1 |  | T | 700 | 1000
480 | 6 | 2 | 1974 | Sosnovyy-Bor, USSR_Russia | USSR_Russia | Energy | Plant | LENINGRAD | 1 | 2 | 4 | 4 | EE | The secondary cooling circuit of Unit 1 ruptured, releasing highly contaminated water into the environment; 3 workers killed (scalded). | LWGR | Operational | 1000 | 1973 |  | 1 |  | 2 |  | T | 20 | 50
481 | 7 | 1 | 1974 | Sosnovyy-Bor, USSR_Russia | USSR_Russia | Energy | Plant | LENINGRAD | 1 | NA |  | 0 | EE | Explosion of the reinforced concrete gas decay tank located outside the block 1 building; no casualties. | LWGR | Operational | 1000 | 1973 | no acute safety relevance - omit (?) | 0 |  | 3 |  | T | 1 | 10
483 |  | 11 | 1973 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 2 | 2 |  | 0 | NA | Five months after unit opened, the unit was shut down when engineers discovered buckling in the steel liner of the concrete dome in which the nuclear reactor is housed. | PWR | Operational | 1067 | 1973 | clearly no CCDF | 0 | Containment | 1 |  | T? | 1 | 10
484 | 7 | 11 | 1973 | Vernon, United States | United States | Energy | Plant | VERMONT YANKEE | Single | 0 |  | 1 | NA | During friction-timing tests following normal refuelling (with open reactor pressure vessel) a control rod was left in the fully withdrawn position and the operator selected a control rod adjacent to that; the reactor reached criticality due to human error but automatically scrammed before any damage or release of radioactivity occurred. | BWR | Permanent Shutdown | 635 | 1972 |  | 0 |  | 1 |  | H | 0 | 0
487 | 11 | 8 | 1973 | South Haven, United States | United States | Energy | Plant | PALISADES | Single | 2 |  | 1 | NA | Steam generator tube leak caused manual shutdown of reactor; outage for repair and resolution of procedural deficiencies extended to 1.1 years. | PWR | Operational | 850 | 1971 |  | ? |  | 1 |  | T | 240 | 400
488 |  | 3 | 1973 | Mihama, Japan | Japan | Energy | Plant | MIHAMA | 1 | 2 |  | ? | A | Broken fuel rods discovered during periodic inspection. | PWR | Permanent Shutdown | 340 | 1970 | Further information desirable to assess plant response and severity. | ? | Fuel rods | 1 |  | T | 1 | 10
491 | 1 | 9 | 1972 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 1 | 1 |  | 1 | NA | Seawater intrusion into the primary system after tubes in the condenser had corroded. Reactor was undergoing a routine startup, operator noted a problem with a demineralizer, switched to a second demineralizer and proceeded with the startup; half an hour later a failure in the second demineralizer apparent and the operator initiated a deliberate shutdown procedure; an hour later excessive chlorides found in primary water and the reactor was scrammed. The main damage was to all of the 120 instruments that measure the power of the reactor. | BWR | Permanent Shutdown | 684 | 1970 | precursor with more serious cost than safety consequences | 1 |  | 2 |  | T | 25 | 50
493 | 13 | 6 | 1972 | Mihama, Japan | Japan | Energy | Plant | MIHAMA | 1 | 2 |  | 1 | A | Steam generator tube leakage was evidenced, and the reactor was stopped for plugging of about 110 tubes and removal of 10 tubes for about a half year. | PWR | Permanent Shutdown | 340 | 1970 | Further information desirable to assess plant response and severity. | 0 |  | 1 |  | T | 70 | 110
496 | 14 | 11 | 1971 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 1,2 | 0;2 |  | 0 | NA | Fire at the unit 2 which was nearing completion, not yet been loaded with fuel. Control rooms of both Unit 1 and 2 contained smoke to the extent that breathing apparatus deemed advisable. Fire caused considerable damage to primary auxiliary building and equipment located there. | PWR | Permanent Shutdown;Operational | 277;1067 | 1962;1973 | clearly no reactor safety problem - costs below threshold (?) - omit | 0 |  | 3 |  | T | 20 | 40
502 | 5 | 6 | 1970 | Morris, United States | United States | Energy | Plant | DRESDEN | 2 | 1 |  | 2 | NA | Starting up phase, doing testing. A spurious signal led to the opening of valves associated with the turbine steam supply, shutting down turbine, causing automatic scram in turn. Reactor water level dropped, feedwater pumps operated intermittently, bypass valves closed, leading to rising water level. Control room indicated low water level and thus operator increased inflow, flooding the main lines. Attempts to shut off inflow partially failed due to leaking valves. Pressure rose, had to manually open relief valuve, jarring adjacent safety valves open. Containment had to be vented to reduce pressure in drywell. The drywell was contaminated, and there was moderate damage to the wire cables and other electrical equipment in the drywell. Down two months for repair. | BWR | Operational | 950 | 1970 | significant cost - complicated physical phenomena and plant-operator-interactions | 1 |  | 2 |  | T | 50 | 80
503 | 15 | 5 | 1970 | Genoa, United States | United States | Energy | Plant | LACROSSE | Single | 2 |  | 1 | NA | A malfunction occurred which closed a valve associated with the steam supply to the turbine; the reactor was normally shutdown but finally automatically scrammed when the pressure began to increase too fast; it was restarted two days later; no injuries or release of radioactivity. | BWR | Permanent Shutdown | 55 | 1968 | secondary - technical - no degradation of safety function - omit (?) | 0 |  | 2 |  | T | 0 | 2
508 | 17 | 10 | 1969 | Saint-Laurent-des-Eaux, France | France | Energy | Plant | ST. LAURENT | A1 | 21 | 4 | 4 | WE | When loading the reactor (at full power), operator erroneously manually (overriding standard procedure since the loading machine correctly stopped the loading) loaded coolant flow restrictor rather than fuel element; part of the uranium fuel (50kg) was damaged and began to melt; contamination of the reactor building/site; continued operation early 1971. | GCR | Permanent Shutdown | 500 | 1969 | Valid precursor, unsure of CCDF | 1 |  | 1 |  | H | 200 | 500
510 | 1 | 5 | 1969 | Agesta, Sweden | Sweden | Energy | Plant | AGESTA | Single | 2 |  | 2 | NE | Rupture of one no-return valve after incorrect switching between two pumps of the recooling system (used to control the temperature of the incoming water from the district heating grid), caused a flood so that the water stream hit the main busbar and caused turbine shutdown; due to short-circuits in the wiring, flooding was not indicated on the control board; flooded cubicle led to numerous undesired system responses; reactor safe shut and cooled down without release. | PHWR | Permanent Shutdown | 12 | 1964 |  | 1 |  | 2 |  | T | 0 | 1
515 | 7 | 2 | 1968 | San Clemente, United States | United States | Energy | Plant | SAN ONOFRE | 1 | 2 |  | 1 to 2 | NA | Fire outside the containment building that damaged penetrating electrical cables caught fire and began to short-circuit; the reactor was shutdown without incident and returned to service after repairs were made; no release of radioactivity. | PWR | Permanent Shutdown | 456 | 1967 | precursor potential to a more serious accident attested | 1 |  | 3 |  | T | 1 | 10
517 | 1 | 5 | 1967 | Annan, United Kingdom | United Kingdom | Energy | Plant | CHAPELCROSS | 2 | 2 | 4 | 4 | WE | Partial meltdown apparently caused when a fuel broke and caught fire; melting of one out of a few thousand fuel channels; reactor closed for two years; release of radioactivity. | GCR | Permanent Shutdown | 60 | 1959 |  | 1 |  | 1 |  | T | 70 | 200
518 | 5 | 10 | 1966 | Lagoona Beach, United States | United States | Energy | Plant | FERMI | 1 | 1 |  | 4 | NA | During power ascension, a zirconium plate at the bottom of the reactor vessel became loose and blocked sodium coolant flow to some fuel subassemblies, out of which two started to melt; manual reactor shut down; no abnormal release; restart three years and nine months later, after clean up and fuel replacement. | FBR | Permanent Shutdown | 65 | 1966 |  | 1 |  | 1 |  | T? | 100 | 200
547 | 20 | 3 | 1978 | Sacramento, United States | United States | Energy | Plant | RANCHO SECO | 1 | 2 |  | 3 | NA | Control console circuit damaged during replacement of lightbulb, leading to loss of power to temp, pressure, and water level monitoring instruments. Common-mode failure. Resultant spurious signals automatically shut of secondary feedwater to SG, which dried out. Emergency aux feedwater started but was stopped by spurious signals. Proper instrumentation restored after 70 minutes. water-level controls in the steam generators had failed, and the steam generators had been flooded up into the steam lines. Makeup water system plus unexpected opening of relief valve maintained cooling. This created a large heat sink for the water in the primary system, and it cooled beyond expectations. The primary and secondary systems were thoroughly examined for damage, but none was found. Four days after the incident the return to full power was started. | PWR | Permanent Shutdown | 917 | 1974 | Serious precursor (CCDF about 0.1) | 1 |  | 1 |  | H | 4 | 8
548 | 9 | 12 | 2005 | Several locations, France | France | Energy | Plant | Several |  | 2 | 2 | 2 | WE | Generic abnormality (all 900 MWe PWR units across 8) that may affect the operation of low-pressure safety injection water pumps and water spray in the enclosure of. In an accident with a leak in the primary circuit of the reactor, the water that escapes is collected at the reactor building from the bottom and returned to the safety injection system to ensure cooling of the reactor. This water, because of its elevated temperature can eventually cause abnormal vibration pumps causing their failure. ASN verified that solution in place by 31 March 2006. | PWR |  |  |  | common cause / generic anomaly | 1 |  | 1 |  | T | 0 | 30
549 | 31 | 12 | 2003 | Several locations, France | France | Energy | Plant | Several |  | 2 | 2 | 2 | WE | Possibility, in large-break LOCA, of filter clogging in recirculation circuit relied on for cooling water from the sump once PTR tank empty . All French nuclear reactors affected, older ones more so due to smaller filtration surfaces. By 2009, filters replaced with larger surfaces at all plants (58 plants, reconstruction of part of the reactor building). | PWR |  |  |  | common cause / generic anomaly (CCF). Baersebeck was forerunner to this. | 1 |  | 1 |  | T | 50 | 600
550 | 12 | 3 | 2001 | Several locations, France | France | Energy | Plant | Several |  | 2 | 2 | 2 | WE | Generic anomaly concerning the valve blockage risk in the recirculation circuit – used to provide cooling water from the sump in the case of a large break LOCA – for some 1300 MWe PWR (12 units). Technical amendments completed in 2003. | PWR |  |  |  | common cause / generic anomaly - check translation | 1 |  | 1 |  | T | 10 | 120
551 | 13 | 8 | 1991 | Scriba, United States | United States | Energy | Plant | NINE MILE POINT | 2 | 2 |  | 1 to 2 | NA | Operating at full power when a fault occurred on phase B of the main transformer which caused the generator, turbine, and reactor to trip; station loads were transferred automatically from the normal station service transformer to the reserve station transformer, which receives power from the grid. During the transient which lasted for about 12 cycles, voltage on the station's phase B buses decreased to approximately 50 percent of normal value before returning to normal. This voltage transient resulted in a loss of power output from five of eight non-safety-related uninterruptible power supplies causing the loss of control room annunciators, relevant information about the plant status and some of the lighting of the plant. Nevertheless, the operators were able to verify that the reactor had tripped and was shut down and to restore power supply. 13 hours later the reactor was in cold shutdown conditions and an hour later the licensee ended the site area emergency. | BWR | Operational | 1320 | 1987 | serious precursor | 1 |  | 2 |  | T | 1 | 10
552 | 25 | 2 | 1983 | Salem, United States | United States | Energy | Plant | SALEM | 1 | 1 |  | 2 | NA | While attempting to bring the unit up to power the operator experienced certain mechanical difficulties and a steam generator transient resulted in a reactor shutdown; an analysis of the event sequence revealed that critical breakers in the automatic shutdown circuits had failed and if the operators had not automatically activated the circuit breakers the event could have resulted in a severe (ATWS-type) event; the outage was caused by inadequate maintenance and supervisory practices. The NRC allowed to restart Salem 1 and required BWR owners to install hardware modifications to make the event less likely and more manageable. | PWR | Operational | 1254 | 1976 | Significant industry impact | 1 |  | 1 |  | T | 800 | 1900
553 | 24 | 2 | 1984 | Salem, United States | United States | Energy | Plant | SALEM | 1 |  |  | 0 | NA | This second Salem 1 outage occurred between February 24, 1984, and May 31, 1984. The record discloses that incompletely cured resins caused certain stator coils to vibrate, eventually resulting in fatigue failure and generator shutdown. It is essentially undisputed that the defective manufacture of the coils was responsible for their ultimate failure. The PUC concluded, however, that the replacement power costs associated with this outage (approximately $27 million) were to be borne by the utility rather than the ratepayers, based on its determination that the ratepayers were not at fault and that PECO was the party most capable of pursuing legal and contractual remedies against the manufacturer, Westinghouse Electric Corporation (Westinghouse). [a33] | PWR | Operational | 1254 | 1976 | liability case - one year outage costs maybe of interest - no safety relevance. | 0 | Generator | 2 | defective manufacturing | H | 120 | 180
554 | 7 | 4 | 1994 | Salem, United States | United States | Energy | Plant | SALEM | 1,2 | 2 |  | 1 | NA | Reactor shut down automatically on April 7 while reactor operators tried to gain control after sea grass clogged the plant's water intakes. When the plant's emergency coolant-injection system activated twice, the utility declared an alert, the third-highest nuclear emergency. Regulators (NRC) blamed the shutdown on a combination of operator error, poor training, previously identified equipment problems and inadequate direction. The NRC is particularly concerned because communications between senior station managment and the staff have been deficient for some time, and the deficiencies have contributed to a number of prior events. During the eight weeks, Salem 1 was shut down, the utilities were forced to buy replacement power at up to $500,000 (1994USD) a day; utilities are spending $150 million to improve equipment and training, in addition to the $300 million spent since 1990. Those costs are shared by the co-owners. | PWR | Operational | 1254;1200 | 1976;1981 | interesting from a costs point of view - only minor safety relevance - omit (?) | ? |  | 1 |  | T | 314.8 | 332.8
556 | 9 | 11 | 1991 | Salem, United States | United States | Energy | Plant | SALEM | 2 | 2 |  | 0 | NA | The main turbine and generator sustained damage when the turbine failed to trip during testing. 'Preventable': a long-unrepaired, known to be degraded, valve inoperative due to mechanical binding. Turbine explosion.[a34,a95] | PWR | Operational | 1200 | 1981 | no safety relevance | 0 |  | 2 |  | T | 130 | 200
559 | 11 | 10 | 1991 | Pripyat, Ukraine | Ukraine | Energy | Plant | CHERNOBYL | 2 | 2 |  | 2? | EE | Chernobyl's Unit 2 was shut down in 1991 after a serious turbine building fire. The authorities subsequently declared the reactor damaged beyond repair, and it was taken offline | LWGR | Permanent Shutdown | 1000 | 1978 | serious precursor | 1 |  | 2 |  | T | 300 | 2000
560 | 9 | 1 | 1982 | Prescott, United States | United States | Energy | Plant | TROJAN | Single | 2 |  | ? | NA | Rupture in feedwater heat extraction line due to erosion resulting in plant shutdown. | PWR | Permanent Shutdown | 1155 | 1975 | Minor safety relevance – lack of detailed information. Cost relevant. | 1 |  | 2 |  | T | 10 | 100
561 | 27 | 1 | 1982 | Vernon, United States | United States | Energy | Plant | VERMONT YANKEE | Single | 2 |  | 0 | NA | Tube degradation. Leak occurred in the 12-in.-diameter drain line between the "C" moisture separator and the heater drain tank, blowing steam into the heater bay area. | BWR | Permanent Shutdown | 635 | 1972 | Cost but not safety relevant | 0 | main feedwater system (turbine building & containment) | 1,2 | tube degradation | T | 1 | 10
562 | 12 | 2 | 1982 | Zion, United States | United States | Energy | Plant | ZION | 1 | 2 |  | 0 | NA | Tube degradation. Steam leak occurred in the 150 psig high-pressure exhaust steam line from the' Unit 1 turbine. The leak originated from an 8-in, crack on a weld joining 24-in.-diameter piping with the 37.5-in.-diameter high pressure steam exhaust pipe leading to the moisture separator reheater. | PWR | Permanent Shutdown | 1085 | 1973 | Cost but not safety relevant | 0 | steam line | 2 | steam erosion | T | 10 | 100
563 | 9 | 11 | 1992 | Prescott, United States | United States | Energy | Plant | TROJAN | Single | 2 |  | 2? | NA | Identified corrosion problems at steam generators gave rise to concerns regarding multiple steam generator leaks and the potential for a main steam line break accident followed by a significant primary-to-secondary leakage that could result in a loss of coolant and damage of the core. Diagnosed sleeve weld circumferential fault causing steam leak, along with widespread corrosion of the steam generators,turned too costly to repair and thus resulting in indefinite shutdown. [587] | PWR | Permanent Shutdown | 1155 | 1975 | potential precursor | 1 |  | 1 |  | T | 1000 | 6500
564 |  |  | 1992 | San Clemente, United States | United States | Energy | Plant | SAN ONOFRE | 1 | 2 |  | 0 | NA | SG tube degradation contributed to the decision to permanently shut down the unit. | PWR | Permanent Shutdown | 456 | 1967 | Cost but not safety relevant | 0 | Steam generator | 1 | tube degradation | T | 790 | 3400
565 | 14 | 4 | 1980 | San Clemente, United States | United States | Energy | Plant | SAN ONOFRE | 1 | 2 |  | 0 | NA | The discovery of corroded and leaking heat exchange tubes during routine maintenance leads to a 14-month shutdown for refueling and $67.7 million worth of repairs to the plant’s steam generators. [a136] | PWR | Permanent Shutdown | 456 | 1967 | Cost but not safety relevant | 0 | Steam generator | 1 | tube degradation | T | 433 | 496
566 | 21 | 11 | 1985 | San Clemente, United States | United States | Energy | Plant | SAN ONOFRE | 1 | 1 |  | 1? | NA | Partial loss of in-plant ac electrical power while the plant was operating at 60 % power. Following a manual reactor trip, the plant lost all in-plant AC power for four minutes and experienced a severe incidence of water hammer in the feedwater system which caused a leak, damaged plant equipment, and challenged the integrity of the plant's heat sink. The most significant aspect of the event involved the failure of five safety related check valves in the feedwater system which appeared in less than a year, without detection, and jeopardized the integrity of safety systems. The event involved a number of equipment malfunctions, operator error, and procedural deficiencies. | PWR | Permanent Shutdown | 456 | 1967 | secondary - partial degradation of safety-related functions - interesting precursor, potential CCF | 1 |  | 2 |  | T | 1 | 10
567 |  | 3 | 1992 | Red Wing, United States | United States | Energy | Plant | PRAIRIE ISLAND | 1 |  |  | 0 | NA | Degraded tube forced 12 day outage. | PWR | Operational | 566 | 1973 | Cost but not safety relevant | 0 | Steam generator | 1 | tube degradation | T | 10 | 20
568 | 2 | 9 | 2009 | Crystal River, United States | United States | Energy | Plant | CRYSTAL RIVER | 3 | NFP |  | NA | NA | Scheduled down time to replace degraded steam generator, allowing for an uprating (planning to restart in April 2011). Operator, Progress Energy, made (unprecedented) choice to manage SG replacement itself, instead of using experienced contractors. A hole was made in the plant's concrete-reinforced steel containment structure for the replacement of its steam generators. This caused part of the concrete to delaminate (60-by-82-foot hourglass-shaped delamination around the opening). Attempts to repair were made, but the problem persisted. Decision to shut down plant in 2013. [a76-a80] | PWR | Permanent Shutdown | 890 | 1977 | Cost but not safety relevant | 0 | Steam generator | 1 | Improper maintenance | H | 3600 | 4100
569 | 2 | 10 | 1987 | Platteville, United States | United States | Energy | Plant | FORT ST. VRAIN | Single | 2 |  | 1 | NA | Hydraulic oil fire broke out in the area of a hydraulic valve (HV-2292) in the turbine building. A manual reactor scram was inserted because of an indicated loss of primary and secondary coolant flow. The fire was extinguished by the plant fire brigade, caused millions of dollars worth of damage. Repairs were made, the reactor was again taken critical on December 11th. | HTGR | Permanent Shutdown | 342 | 1976 | Cost but not safety relevant | 0 |  | 2 |  | T | 16 | 19
570 | 18 | 8 | 1989 | Platteville, United States | United States | Energy | Plant | FORT ST. VRAIN | Single | 2 |  | 0 | NA | During routine surveillance testing a control rod drive assembly was found to malfunction. The plant was shut down and preparations for repair and return to service were begun. However, during a routine walkdown by one of the plant engineers, hairline cracks were found in the inconel steel main steam ring header immediately below the reactor. This ring header received steam from the steam generators in the reactor prior to the steam's short trip to the turbine generator. The hairline cracks proved to be the last straw for Fort St. Vrain. Based on this turn of events, the PSC Board of Directors announced the decision to terminate operations at Fort St. Vrain effective on August 29, 1989. | HTGR | Permanent Shutdown | 342 | 1976 | Cost but not safety relevant | 0 | control rod drive assembly, main steam ring header | 1 |  | T | 700 | 1550
571 | 5 | 7 | 2001 | Annan, United Kingdom | United Kingdom | Energy | Plant | CHAPELCROSS | 3 | NFP |  |  | WE | During routine defuelling activities on Reactor 3, a basket containing twenty-four low rated irradiated Magnox fuel elements had fallen 80 ft (24.4m) into the fuel discharge well. | GCR | Permanent Shutdown | 60 | 1959 |  | 0 | defuelling equipment | 1? |  | T | 100 | 500
572 |  |  | 1968 | Agesta, Sweden | Sweden | Energy | Plant | AGESTA | Single | 2 |  | 1 to 2 | NE | Major fuel damage event after spacer grid spring relaxation and flow vibration. 15 fuel assemblies failed. Reactor returned to service with modified fuel. | PHWR | Permanent Shutdown | 12 | 1964 |  | 1 |  | 1 |  | T | 1 | 20
574 | 10 | 10 | 1969 | Saint-Laurent-des-Eaux, France | France | Energy | Plant | ST. LAURENT | A1 | 1 |  | 1 | WE | The day after its official inauguration, a human and technical handling error caused a cylinder of graphite, used in the initial phase to control core reactivity, to enter a channel filled with fuel elements. Its presence interrupted their cooling, causing two new fuel elements to melt. There was no effect on the environment, but the reactor was out of operation for one year. | GCR | Permanent Shutdown | 500 | 1969 |  | 0 |  | 1 |  | T | 180 | 300
575 | 13 | 2 | 1980 | Saint-Laurent-des-Eaux, France | France | Energy | Plant | ST. LAURENT | A1 | 1 |  | 1 | WE | During startup a faulty measurement of gas temperature at the core exit, combined with human error and unusual physical conditions (xenon effect, rod position and moderator temperature) which greatly distorted the axial flux curve, caused cladding to begin melting in 33 core channels. This accident had no effect on reactor operation or on the environment. [a93] | GCR | Permanent Shutdown | 500 | 1969 |  | 0 |  | 1 |  | T;H | 10 | 50
577 | 28 | 6 | 1980 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 3 | 2 |  | 2 | NA | 76 of the 185 control rods failed to fully insert during a routine shutdown at TVA's Browns Ferry Unit No 3 located at Athens Alabama. The reactor was manually scrammed from about 30 percent power in accordance with routine shutdown procedures. The shutdown was initiated to repair the feedwater system. The 76 control rods that failed to fully insert were all on the east side of the core. Following scram discharge volume (SDV) high level bypass and a short drain period of the SDV, a second manual scram was initiated and all partially inserted rods were observed to drive inward, but 59 remained partially withdrawn. A third manual scram was made, again following high level in the SDV and bypassing for another short drain of the SDV, with the result that 47 rods remained partially withdrawn. Following a longer drain of the SDV, an automatic scram occurred that was initiated by a scram discharge volume tank high water level signal when the scram reset switch was placed in "Normal"; with this scram all remaining rods fully inserted. The total time elapse from the initial scram to the time that all rods were inserted was approximately 15 minutes. Core coolant flow, temperature and pressure remained normal for plant conditions. The unit is now shutdown and additional testing indicates that a possible cause of the malfunction was the retention of a significant amount of water in the east bank scram discharge volume. | BWR | Operational | 1155 | 1976 | ATWS precursor | 1 |  | 1 |  | T | 0 | 1
578 |  |  | 1982 | Monticello, United States | United States | Energy | Plant | MONTICELLO | Single | 2 |  | 1 | NA | Cracking in recirculation piping was discovered in the 22-inch manifold and 12-inch riser piping (in 1983, the stainless steel piping in the recirculation system and several connected branch systems was replaced). | BWR | Operational | 691 | 1971 | IGSCC materials problem detected during inspection | 0 |  | 1 |  | T | 480 | 750
581 | 22 | 8 | 2013 | Plymouth, United States | United States | Energy | Plant | PILGRIM | 1 | 2 |  | 1 | NA | Manually scrammed due to lowering reactor water level resulting from a trip of all three of the reactor feed pumps, due to a loss of power to the pump seal cooling water flow switch relays and resultant automatic actuation of the feed pump trip circuit. Corrective action was taken to repair the ground fault in the associated circuits and to revise reactor feed pump trip circuit design. With the plant online at 98% power, all three of the plant's main feedwater pumps tripped causing a drop of the reactor water level. The reactor subsequently tripped. The loss of feedwater and sudden trip from the high power level caused the reactor water level to drop below -46 inches. After passing this point, the emergency core cooling system automatically activated. The RCIC and HPCI systems promptly restored the reactor water level to normal. | BWR | Operational | 711 | 1972 |  | 1 |  | 1 |  | T | 6 | 10
582 | 22 | 10 | 2009 | Avila Beach, United States | United States | Energy | Plant | DIABLO CANYON | 2 | 2 |  | 2 | NA | A botched valve repair prevented other key valves from opening; tests after the valve repairs failed to detect the problem; the reactor operated for nearly 18 months with systems that provide emergency cooling water to the core and containment vessel disabled. | PWR | Operational | 1197 | 1985 | near-miss candidate for precursor study | 1 |  | 1 |  | H | 0 | 0
584 |  | 3 | 1999 | Leiston, United Kingdom | United Kingdom | Energy | Plant | SIZEWELL | B | 0 |  | 1 | WE | Shortly after the reactor was shut down for a refuelling outage, a large quantity of reactor coolant system water was released to the containment building during in-situ testing of a safety relief valve. There were no injuries and no release of radiation outside the containment. As a result of investigations by the licensee and by NII these valves are now removed for testing to a separate test facility and many of the station operating instructions were amended to better aid the operators in their response to alarms. [a120] | PWR | Operational | 1250 | 1995 |  | 0 |  | 1 |  | H | 0 | 1
586 |  |  | 2009 | Geesthacht, Germany | Germany | Energy | Plant | KRUEMMEL | Single | 2 |  | 0 | WE | Electrical transformer fire, just weeks after coming back online following similar incident, led to shutdown. Plan to buy two new transformers and install in Spring 2010. Plans dropped after 2011 decision to shut all 17 German NPP by 2022. Vattenfall 2015 submitted an application to decommission and dismantle. Shutdown led to a partial blackout in Hamburg (for an hour): In the big city the largest part of the traffic light systems failed, shopping centers lacked hourlight. Because water pumps were also lame because of the power failure, the result was pipebreaks, which meant that many households were cut off from the water supply. The Atomic Authority in Kiel ordered a "reliability test" from the operator Vattenfall. The shutdown of Kruemmel has prompted Environment Minister Sigmar Gabriel to call for the immediate closure of the eight oldest plants. [a122, a123] | BWR | Permanent Shutdown | 1402 | 1983 | no safety relevance | 0 | Transformer | 2 |  | T | 1600 | 2000
587 | 13 | 4 | 1979 | Barseback, Sweden | Sweden | Energy | Plant | BARSEBACK | 1 | 2 |  | 0 | NE | The water retaining ring of the generator broke due to stress corrosion and caused massive damage to the generator, the turbine unit and the turbine hall; the short circuit ignited lubricating oil and caused a fire around the generator and destroying some cables. | BWR | Permanent Shutdown | 615 | 1975 | Cost but not safety relevant | 0 |  | 2 |  | T | 305 | 340
588 | 17 | 3 | 1984 | San Clemente, United States | United States | Energy | Plant | SAN ONOFRE | 3 | 2 |  | 1 | NA | During routine surveillance at approximately 100% power, manual isolation valves in both of the containment spray headers were found closed, rendering both trains of the containment spray system (CSS) inoperable. Misalignment of the isolation valves was caused by improper use of the valve alignment checklist for the CSS when leaving the shutdown cooling mode. Plant is fined $125,000 because cooling system valves were closed during full operation. | PWR | Permanent Shutdown | 1127 | 1983 | degradation of heat removal function of containment, not directly core related - primary, human | 0 |  | 1 |  | H | 0 | 0
589 | 19 | 3 | 1984 | Sacramento, United States | United States | Energy | Plant | RANCHO SECO | 1 | 2 |  | 1 | NA | The loss of the hydrogen side sealing oil pump and other problems in the sealing oil system resulted in the escape of hydrogen from the generator. Hydrogen escaped for several minutes before it exploded; the following fire burned for five to eight minutes. Reactor shutdown. | PWR | Permanent Shutdown | 917 | 1974 | No major safety, but cost relevance. | ? |  | 2 |  | T | 50 | 100
590 | 1 | 7 | 1985 | Heng Chun, Taiwan, China | Taiwan, China | Energy | Plant | MAANSHAN | 1 | 2 |  | 1 | A | Due to torsional vibrations of generator's rotor some LP turbine's blades broke. Rotor got into unbalance which caused break down of generator sealings; leaking hydrogen and oil caught fire. Generator and exciter were damaged badly; plant shut down. | PWR | Operational | 951 | 1984 | No major safety, but cost relevance. | 0 |  | 2 |  | T | 500 | 1000
592 |  |  | 2016 | Several locations, France | France | Energy | Plant | Several |  |  |  | ? | WE | The French nuclear safety authority (ASN) has requested five of EDF's nuclear power units are taken offline for additional inspections on their steam generators within the next three months. The steel in parts of those components has been found to contain high concentrations of carbon. In June, the ASN said it had identified 18 French nuclear power reactors operated by EDF - of both 900 and 1450 MWe capacity - whose steam generators could contain high carbon concentrations. ASN said EDF has provided it with data aimed at demonstrating the operating safety of the 12 reactors concerned. ASN now requires inspections at the remaining five units which can only be conducted when the reactors are offline, must be performed "without waiting for the scheduled refuelling outage of these reactors". | PWR |  |  |  | Safety relevance still unknown. Costly. | ? | Steam generator | 1 |  | T | 2600 | 4000
595 | 3 | 8 | 2001 | Pope, United States | United States | Energy | Plant | ANO | 1 | ? |  | 1 | NA | Fire protection and procedures were inadequate for the north switchgear room, Fire Zone 99-M | PWR | Operational | 903 | 1974 |  | 1 | Switchgear room | 2 | deficient procedure | H | 0 | 0
596 | 24 | 3 | 2001 | Pope, United States | United States | Energy | Plant | ANO | 1 | ? |  | 1 | NA | RPV head leakage due to PWSCC of one CRDM nozzle. | PWR | Operational | 903 | 1974 |  | 1 | RPV head | 1 | PWSCC | T | 10 | 50
600 | 22 | 2 | 2015 | Pope, United States | United States | Energy | Plant | ANO | 1,2 | ? |  | 2 | NA | Inadequate External Flood Protection for Safety-Related Equipment Located Below the Design Basis Flood Elevation. | PWR | Operational | 903;1065 | 1974;1978 |  | 1 | auxiliary building and emergency diesel fuel storage building | 3 | deficient design & procedure | H | 0 | 1
601 | 24 | 6 | 2009 | Braidwood, United States | United States | Energy | Plant | BRAIDWOOD | 1 | ? |  | 1 | NA | Failure of containment sump suction valve to open. | PWR | Operational | 1270 | 1987 |  | 0 | Safety injection system | 1 | Inadequate training | H | 1 | 10
602 | 16 | 4 | 2002 | Braidwood, United States | United States | Energy | Plant | BRAIDWOOD | 1 | ? |  | 1 | NA | Inoperable power operated relief valve (PORV) bleedpath due to leaking air accumulators. | PWR | Operational | 1270 | 1987 |  | 1 | Pressurizer | 1 | Improper maintenance | H | 0 | 1
606 | 23 | 10 | 2010 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 1 | ? |  | 2 | NA | Failure to establish adequate design control and perform adequate maintenance causes valve failure that led to a residual heat removal loop being unavailable. | BWR | Operational | 1155 | 1973 |  | 1 | Emergency Core Cooling System (ECCS) | 1 | inadequate design control & maintenance | H | 0 | 1
608 | 22 | 12 | 2012 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 2 | ? |  | 1 | NA | Unplanned automatic reactor scram due to loss of power to the reactor protection system. | BWR | Operational | 1155 | 1974 |  | 0 | Reactor Protection System | 1 | Inadequate training | H | 7 | 9
610 | 22 | 5 | 2012 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 3 | ? |  | 1 | NA | Reactor trip and subsequent loss of offsite power caused by failure of unit station system transformer differential relay. | BWR | Operational | 1155 | 1976 |  | 1 | Power supply: Unit Station Service Transformer (USST) | 2? | incorrect design calculation settings | H | 6 | 8
611 | 20 | 1 | 2010 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 1,2,3 | ? |  | 2 to 3 | NA | Failure to protect cables of redundant safety systems from fire damage. | BWR | Operational | 1155 | 1973;1974;1976 |  | 1 | safety system (necessary to achieve and maintain hot shutdown conditions) | 1 | inadquate design | H | 0 | 0
612 | 23 | 12 | 2008 | Decatur, United States | United States | Energy | Plant | BROWNS FERRY | 1,2,3 | ? |  | 1 | NA | Inadequate procedure revision could lead to failure in operator response to a fire. | BWR | Operational | 1155 | 1973;1974;1976 |  | 0 | reactor vessle | 1 | inappropriate procedure | H | 0 | 0
614 | 20 | 4 | 2011 | Southport, United States | United States | Energy | Plant | BRUNSWICK | 1 or 2 | ? |  | 1 | NA | Penetrations in exterior wall of EDG fuel oil structure could lead to failure of the EDGs during postulated flooding. | BWR | Operational | 990 or 960 | 1976 or 1975 |  | 0 | EDG fuel oil tank room | 3? | Inadequate inspection & maintenance | H | 0 | 1
615 | 2 | 11 | 2006 | Southport, United States | United States | Energy | Plant | BRUNSWICK | 1 | ? |  | 1 | NA | Emergency diesel generator inoperable due to failure of foreign material exclusion practices. | BWR | Operational | 990 | 1976 |  | 0 | EDG | 1 | inadequate post-maintenance closeout inspections | H | 0 | 0
616 | 7 | 6 | 2007 | Southport, United States | United States | Energy | Plant | BRUNSWICK | 1,2 | ? |  | 1 | NA | All emergency diesel generators unable to be operated locally due to incorrect control relaywiring. | BWR | Operational | 990;960 | 1976;1975 |  | 0 | EDG | 1 | Improper maintenance | H | 0 | 1
617 | 19 | 4 | 1981 | Southport, United States | United States | Energy | Plant | BRUNSWICK | 1 | ? |  | 2 | NA | RHR heat exchanger damaged. While the reactor was in cold shutdown during a maintenance outage, the normal decay heat removal system was lost because of a failure of the single RHR heat exchanger that was currently in service. The failure occurred when the starting of a second RHR service water pump caused the failure of a baffle in the waterbox of the RHR heat exchanger, thereby allowing cooling water to bypass the tube bundle. The redundant heat exchanger was inoperable because maintenance was in progress. | BWR | Operational | 990 | 1976 |  | 1 | RHR | 1 |  | T | 1 | 10
619 | 29 | 4 | 1975 | Southport, United States | United States | Energy | Plant | BRUNSWICK | 2 | ? |  | 2 | NA | Multiple valve failures; RCIC inoperable as a result of stuck-opendown/safety valve at 10-percent power, the RCIC system was determined to be inoperable, and SRV B was stuck open. The operator failed to scram the reactor according to the emergency operating procedures (EOPs). The HPCI system failed to run and was manually shut down as a result of high torus level. Loop B of RHR failed as a result of a failed service water supply valve to the heat exchanger.The reactor experienced an automatic scram on manual closure of the MSIV. | BWR | Operational | 960 | 1975 |  | 1 | ECCS (RCIC, HPCI, RHR) | 1 |  | ?
620 | 4 | 1 | 2004 | Southport, United States | United States | Energy | Plant | BRUNSWICK | 1 | ? |  | 1 | NA | EDG 3 unavailable due to jacket water leak. | BWR | Operational | 990 | 1976 |  | 1 | EDG | 1 | Improper maintenance | H | 0 | 1
621 | 19 | 10 | 2007 | Byron, United States | United States | Energy | Plant | BYRON | 1,2 | ? |  | 1 | NA | On October 19, 2007, the riser piping of the C cell in the OA tower was being cleaned of corrosion buildup in order to obtain accurate ultrasonic wall thickness examinations. During the course of this cleaning effort, a small hole was created in the pipe and it started to spray water. The leak was estimated as 10 gpm. The pipe was declared inoperable. This section of pipe cannot be isolated from the other cells on the OA tower, consequently the OA tower (i.e., four cells) was also declared inoperable. | PWR | Operational | 1242;1210 | 1985;1987 |  | 0 | Ultimate Heat Sink | 2 | piping degration & inadequate maintenance | T;H | 50 | 70
622 | 17 | 11 | 2010 | Byron, United States | United States | Energy | Plant | BYRON | 2 | ? |  | 1 | NA | Failure to ensure that a flange connection on the EDG lube oil cooler was correctly torqued following maintenance. | PWR | Operational | 1210 | 1987 |  | 0 | EDG | 1 | Improper maintenance | H | 0 | 1
624 | 14 | 2 | 2001 | Fulton, United States | United States | Energy | Plant | CALLAWAY | 1 | ? |  | 1 | NA | Concurrent unavailabilities, potential unavailability of ESW Pump and MDAFW Pump due to foreign material and CCW Pump out for test and maintenance. | PWR | Operational | 1275 | 1984 |  | 1 | Essential Service Water (ESW) system | 1 | Human performance & procedure deficiency | H | 0 | 0
625 | 16 | 5 | 2001 | Lusby, United States | United States | Energy | Plant | CALVERT CLIFFS | 1 | ? |  | 1 | NA | TDAFW pump inoperable due to sealant intrusion. | PWR | Operational | 918 | 1975 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 | Incorrect instruction on vendor manual | H | 0 | 1
626 | 24 | 3 | 2006 | Lusby, United States | United States | Energy | Plant | CALVERT CLIFFS | 1 | ? |  | 1 to 2 | NA | Degraded EDG caused by inadequate feeder breaker. | PWR | Operational | 918 | 1975 |  | 0 | EDG | 1 | Incorrect setpoint | H | 0 | 1
627 | 13 | 4 | 1978 | Lusby, United States | United States | Energy | Plant | CALVERT CLIFFS | 1 | 0 |  | 2 | NA | With the plant shutdown, a protective relay automatically opened the switchyard breakers, resulting in a LOOP. EDG "11" failed to start. EDG "22" started and supplied the safety buses. | PWR | Operational | 918 | 1975 |  | 1 | EDG, Switchyard | 1,2 |  | ?
628 | 23 | 1 | 2004 | Lusby, United States | United States | Energy | Plant | CALVERT CLIFFS | 2 | ? |  | 1 | NA | Reactor trip caused by loss of main feedwater and complicated by a failed relay causing overcooling. | PWR | Operational | 911 | 1976 |  | 1 | steam generator feed pump | 2 |  | T | 3 | 5
630 | 20 | 5 | 2006 | York County, United States | United States | Energy | Plant | CATAWBA | 1,2 | ? |  | 1 to 2 | NA | Dual Unit LOOP. | PWR | Operational | 1188 | 1985;1986 |  | 1 | Switchyard | 2 | Inadequate maintenance | H | 56 | 70
631 | 4 | 4 | 2012 | York County, United States | United States | Energy | Plant | CATAWBA | 1,2 | ? |  | 1 | NA | Reactor trip caused by faulted reactor coolant pump cable and an error in protective relay. | PWR | Operational | 1188 | 1985;1986 |  | 1 | Reactor coolant pump, switchyard | 1,2 | thermal degradation, design error | T;H | 25 | 30
632 | 13 | 6 | 1986 | York County, United States | United States | Energy | Plant | CATAWBA | 1 | ? |  | 2 | NA | Chemical and volume control system (CVCS) leak (130 gpm) from the component cooling water (CCW)/CVCS heat exchanger joint (i.e.,small-break loss-of-coolant accident (LOCA))A weld break on the letdown piping, near the CCW/CVCS heat exchanger caused excessive RCS leakage. A loss of motor control center (MCC)power caused the variable letdown orifice to fail open. The weld on the 1-inch (2.54-cm) outlet flange on the variable letdown orifice failed as aresult of excessive cavitation-induced vibration. This event was a small-break LOCA. | PWR | Operational | 1188 | 1985 |  | 1 | Reactor Coolant (NC) System | 1 |  | T | 10 | 30
633 | 6 | 2 | 1996 | York County, United States | United States | Energy | Plant | CATAWBA | 2 | ? |  | 2 | NA | When the reactor was at hot shutdown, a transformer in the switchyard shorted out during a storm, causing breakers to open and resulting in a loss of offsite power(LOOP) event. Although both emergency diesel generators (EDGs) started, the output breaker of EDG "1B" to vital Bus "1B" failed to close on demand, leaving Bus "1B" without power. After 2 hours and 25 minutes, operators successfully closed the EDG "1B" output breaker. | PWR | Operational | 1188 | 1986 |  | 1 | Main Transformers | 2 | Unsuitable resistor bushings; Inadequate preventative maintenance | T;H | 5 | 10
634 | 20 | 1 | 2006 | Hart Township, United States | United States | Energy | Plant | CLINTON | 1 | ? |  | 1 to 2 | NA | Potential air entrapment of HPCS because of incorrect suction source switchover setpoint. | BWR | Operational | 1098 | 1987 |  | 0 | high pressure core spray (HPCS) | 1 | Inadequate design | H | 0 | 0
635 | 14 | 2 | 2002 | Bento, United States | United States | Energy | Plant | COLUMBIA | Single | ? |  | 1 | NA | Potential unavailability of four safety-related breakers due to degraded MOC switches. | BWR | Operational | 1190 | 1984 |  | 1 | EDG | 1 | Inadequate maintenance | H | 15 | 25
636 | 23 | 6 | 2005 | Bento, United States | United States | Energy | Plant | COLUMBIA | Single | ? |  | 1 | NA | Reactor trip due to feedwater pump trip cause by maintenance personnel error. | BWR | Operational | 1190 | 1984 |  | 1 | reactor feedwater pump | 2 | Improper maintenance | H | 18 | 24
638 | 21 | 11 | 2007 | Glen Rose, United States | United States | Energy | Plant | COMANCHE PEAK | 1 | ? |  | 0 to 1 | NA | Emergency diesel generator failed to activateduring testing. | PWR | Operational | 1259 | 1990 |  | 0 | EDG | 1 | Improper maintenance | H | 0 | 1
639 | 11 | 6 | 1999 | Bridgman, United States | United States | Energy | Plant | COOK | 1,2 | ? |  | 1 | NA | Lack of capability to operate emergency service water following a seismic event (Inspection reports 50-315/316/97-024 and 50-315/316/99-010) | PWR | Operational | 1131;1231 | 1975;1978 |  | 1 | Natural hazard: seismic | 3 |  | ? | 0 | 0
640 | 30 | 12 | 1999 | Bridgman, United States | United States | Energy | Plant | COOK | 1,2 | ? |  | 1 | NA | Valves required to operate post-accident could fail to open due to pressure-locking/thermal binding. | PWR | Operational | 1131;1231 | 1975;1978 |  | 1 | Emergency Core Cooling System (ECCS) | 1 | inadequate design review | H | 0 | 1
642 | 29 | 8 | 2001 | Bridgman, United States | United States | Energy | Plant | COOK | 1,2 | ? |  | 1 | NA | Concurrent unavailabilities. EDGs potentially unavailable due to lack of essential service water (ESW) flow caused by a deformed SW strainer and TDAFW pump inoperable due to failed latching mechanism. | PWR | Operational | 1131;1231 | 1975;1978 |  | 1 | Essential Service Water (ESW) system | 1 | Material failure, Inadeuate design & maintenance | T;H | 70 | 90
643 | 22 | 1 | 1998 | Bridgman, United States | United States | Energy | Plant | COOK | 1,2 | ? |  | 1 | NA | Postulated high-energy line break in turbine building leading to failure of all component cooling water pumps. | PWR | Operational | 1131;1231 | 1975;1978 | <LC> incorrect source or description | 1 | safety-related ice condenser system | 1 |  | T | 1 | 10
644 |  |  |  | Bridgman, United States | United States | Energy | Plant | COOK | 2 |  |  |  | NA | Potential failure of all component cooling water pumps due to steam intrusion resulting from a postulated high-energy line break | PWR | Operational | 1231 | 1978 | <LC> ref/source missing | ?
645 | 22 | 10 | 1999 | Bridgman, United States | United States | Energy | Plant | COOK | 1,2 | ? |  | 3 | NA | Potential high-energy line break conditions affecting the operability of mitigating systems. | PWR | Operational | 1131;1231 | 1975;1978 |  | 1 | Multiple | 1,2 | inadequate design and licensing basis control | H | 0 | 0
646 | 18 | 1 | 2007 | Brownville, United States | United States | Energy | Plant | COOPER | Single | ? |  | 1 | NA | Inadequate procedures result in failure of emergency diesel generator voltage regulator. | BWR | Operational | 801 | 1974 |  | 0 | EDG | 1 | Inadequate procedure | H | 0 | 10
647 |  | 6 | 2007 | Brownville, United States | United States | Energy | Plant | COOPER | Single | ? |  | 1 to 2 | NA | Inadequate post-fire procedure could have prevented achieving safe shutdown. | BWR | Operational | 801 | 1974 |  | 0 |  | NA | Inadequate procedure | H | 0 | 0
648 | 15 | 1 | 2008 | Brownville, United States | United States | Energy | Plant | COOPER | Single | ? |  | 1 | NA | Failure to establish procedural controls for maintenance of electrical connections on essential equipment. | BWR | Operational | 801 | 1974 |  | 0 | EDG | 1 | Inadequate maintenance | H | 0 | 0
649 |  | 10 | 2010 | Brownville, United States | United States | Energy | Plant | COOPER | Single | ? |  | 1 to 2 | NA | Deficient emergency procedures could lead to operators failing to position valves necessary for core cooling during a postulated fire. | BWR | Operational | 801 | 1974 |  | 1 | Core cooling | 1 | Inadequate procedure | H | 0 | 0
650 | 31 | 8 | 1977 | Brownville, United States | United States | Energy | Plant | COOPER | Single | ? |  | 2 | NA | A blown fuse caused the normal power supply to the feedwater and RCIC controllers to fail. The alternate power supply was unavailable due to an unrelated fault. A partial loss of feedwater occurred, and the reactor tripped on low water level. RCIC and HPCI operated; however,both pumps did not accelerate to full speed (RCIC due to the failed power supply and HPCI due a failed governor actuator). | BWR | Operational | 801 | 1974 |  | 1 | Normal power supply to the feedwater and RCIC controllers | 1 |  | T
651 | 1 | 10 | 2001 | Crystal River, United States | United States | Energy | Plant | CRYSTAL RIVER | 3 | ? |  |  | NA | RPV head leakage due to PWSCC of one CRDM nozzle. | PWR | Permanent Shutdown | 890 | 1977 |  | 1 | RPV head | 1 | PWSCC | T | 5 | 15
652 | 27 | 1 | 2005 | Crystal River, United States | United States | Energy | Plant | CRYSTAL RIVER | 3 | ? |  | 1 | NA | Single-failure vulnerability of 4160 V engineered safeguard feature (ESF) bus protective relay schemes caused by common power metering circuits. | PWR | Permanent Shutdown | 890 | 1977 |  | 1 | EDG, offsite power supply | 1,2 | Inadequate design | H | 0 | 1
653 | 26 | 2 | 1980 | Crystal River, United States | United States | Energy | Plant | CRYSTAL RIVER | 3 | ? |  | 2 | NA | Loss of 24-volt DC power to non-nuclear instrumentation (NNI). The 24-volt power supply to the NNI was lost as a result of a short to ground. This initiated a sequence of events in which the PORV opened (and stayed open) as a direct result of the loss of the NNI power supply. HPI initiated as a result of depressurization through the open PORV, and with approximately 70 percent of NNI inoperable or inaccurate, the operator correctly decided that there was insufficient information available to justify terminating HPI. Therefore, the pressurizer was pumped solid, one safety valve lifted, and flow through the safety valve was sufficient to rupture the reactor coolant drain tank rupture disk, thereby spilling approximately 43,000 gallons (162,800 liters) of primary water into the containment. | PWR | Permanent Shutdown | 890 | 1977 |  | 1 | non-nuclear instrumentation power supply | 2 |  | T | 1 | 10
655 | 19 | 4 | 1980 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | ? |  | 2 | NA | When the reactor was in cold shutdown, two essential buses were lost due to breaker ground fault relay actuation during an electrical lineup. Decay heat drop line valve was shut, and air was drawn into the suction of the decay heat removal pumps, resulting in loss of a decay heat removal path. | PWR | Operational | 925 | 1977 |  | 1 | essential distribution panels | 1? |  | T | 0 | 0
656 | 24 | 6 | 1981 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | ? |  | 2 | NA | With the plant at 74% power, the loss of Bus β€E2β€™ occurreddue to a maintenance error during CRDM breaker logic testing. A reactor trip occurred, due to loss of CRDM power (Bus β€E2β€™), and instrumentation power was also lost(Bus β€E2β€™ and a defective logic card on the alternate source). During the recovery, AFW Pump β€2β€™ failed to startdue to a maladjusted governor slip clutch and bent lowspeed stop pin. A main steam safety valve lifted, andfailed to reseat. | PWR | Operational | 925 | 1977 |  | 1 | CRDM power & Instrumentation power | 1 | Maintenance error | H | 10 | 50
657 | 14 | 10 | 1998 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | ? |  | 1 | NA | Manual reactor trip while recovering from a component cooling system leak and deenergization of safety-related bus D1 and nonsafety bus D2. | PWR | Operational | 925 | 1977 |  | 1 |  | 1 |  | T | 8 | 15
660 | 11 | 12 | 1977 | Ottawa, United States | United States | Energy | Plant | DAVIS BESSE | 1 | ? |  | 2 | NA | During AFW pump testing, operators found that control over both pumps was lost because of mechanical binding in the governor of one pump and blown control power supply fuses for the speed changer motor on the other pump. | PWR | Operational | 925 | 1977 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 |  | T?
662 | 15 | 5 | 2000 | Avila Beach, United States | United States | Energy | Plant | DIABLO CANYON | 1 | ? |  | 2 | NA | Extended loss of offsite power to safety-related buses due to 12-kV bus fault. | PWR | Operational | 1197 | 1984 |  | 1 | Power supply: loss of both sources of offsite power to vital loads | 1 | long-term degradation, and/or inadequate preventive maintenance | T;H? | 25 | 50
664 | 30 | 1 | 2004 | Morris, United States | United States | Energy | Plant | DRESDEN | 2,3 | ? |  | 1 | NA | HPCI potentially unavailable due to water carryover into steam line caused by feedwater level control failure. | BWR | Operational | 950;935 | 1970;1971 |  | 1 | HPCI, Main turbine | 1,2 | Inadequate procedure | H | 4 | 5
666 | 21 | 11 | 2012 | Morris, United States | United States | Energy | Plant | DRESDEN | 2,3 | ? |  | 2 | NA | Failure to establish procedure to address the effect of external flooding on the plant. | BWR | Operational | 950;935 | 1970;1971 |  | 1 | Natural hazards: flooding | 3 | Inadequate procedure | H | 0 | 0
667 | 5 | 7 | 2001 | Morris, United States | United States | Energy | Plant | DRESDEN | 3 | ? |  | 1 | NA | HPCI inoperable due to water hammer event. | BWR | Operational | 935 | 1971 |  | 1 | HPCI | 1 |  | T;H | 2 | 5
668 | 5 | 5 | 2004 | Morris, United States | United States | Energy | Plant | DRESDEN | 3 | ? |  | 1 | NA | Plant-centered LOOP due to breaker malfunction. | BWR | Operational | 935 | 1971 |  | 1 | Switchyard | 2 |  | T | 7 | 10
670 | 13 | 3 | 2008 | Dothan, United States | United States | Energy | Plant | FARLEY | 1 | ? |  | 1 | NA | Emergency diesel generator exhaust pipe failure. | PWR | Operational | 918 | 1977 |  | 0 | EDG | 1 | defective manufacturing | H | 0 | 1
671 | 25 | 3 | 1978 | Dothan, United States | United States | Energy | Plant | FARLEY | 1 | ? |  | 2 | NA | Low water level in one SG trip/scram; turbine-driven EFW pump fails. A low-level condition in a single SG resulted in a reactor trip. The turbine-driven EFW pump failed to start. Both motor-driven EFW pumps started, but were deemed ineffective because all recirculation bypass valves were open (thereby diverting flow). A recirculation valve was manually closed. | PWR | Operational | 918 | 1977 |  | 1 | Steam generator, EFW pump | 1,2 |  | ?
672 | 5 | 1 | 2007 | Dothan, United States | United States | Energy | Plant | FARLEY | 2 | ? |  | 1 to 2 | NA | Residual heat removal containment sump suction valve inoperable for 85 days. | PWR | Operational | 928 | 1981 |  | 1 | Containment to RHR | 1 | Inadequate maintenance | H | 0 | 1
673 | 14 | 8 | 2003 | Lagoona Beach, United States | United States | Energy | Plant | FERMI | 2 | ? |  | 1 | NA | Reactor trip and loss of offsite power occurred as a result of the power blackout in the Northeast United States on August 14, 2003. | BWR | Operational | 1198 | 1986 |  | 1 | Offsite power blackout | 3 |  | T | 13 | 17
674 | 28 | 3 | 2001 | Lagoona Beach, United States | United States | Energy | Plant | FERMI | 2 | ? |  | 1 | NA | EDG unavailable due to degraded bearing. | BWR | Operational | 1198 | 1986 |  | 1 | EDG | 1 | Improperly used / inadequate process | H | 0 | 10
675 | 14 | 8 | 2003 | Oswego, United States | United States | Energy | Plant | FITZPATRICK | Single | ? |  | 1 | NA | Reactor trip and loss of offsite power occurred as a result of the power blackout in the Northeast United States on August 14, 2003. | BWR | Operational | 849 | 1975 |  | 1 | Offsite power blackout | 3 |  | T | 6 | 8
676 |  |  | 2010 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | ? |  | 2 | NA | Failure to establish and maintain procedures to protect the heat sink cooling water intake structure and auxiliary building from external floods. | PWR | Permanent Shutdown | 512 | 1973 |  | 1 | Natural hazards: external flood | 3 | Inadequate procedure | H | 1 | 10
677 |  | 10 | 2013 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | ? |  | 1 to 2 | NA | Harsh environment due to postulated high-energy line breaks could lead to the failure of equipment needed to safely shutdown the plant. | PWR | Permanent Shutdown | 512 | 1973 |  | 1 | Safe shutdown system | 1 | Inadequate design | H | 0 | 0
678 | 19 | 10 | 2004 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | ? |  | 1 | NA | EDG 2 inoperable for 28 days due to blown fuse. | PWR | Permanent Shutdown | 512 | 1973 |  | 1 | EDG | 1 |  | T | 0 | 0
680 | 11 | 5 | 2005 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | ? |  | 1 | NA | Faulty maintenance causes the inoperability of a containment spray train for 454 days. | PWR | Permanent Shutdown | 512 | 1973 |  | 0 | Containment spray | 1 | Improper maintenance | H | 0 | 0
681 | 14 | 2 | 2007 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | ? |  | 1 | NA | Emergency diesel generator failure during test due to degraded field flash contacts. | PWR | Permanent Shutdown | 512 | 1973 |  | 0 | EDG | 1 | Inadequate maintenance | H | 0 | 0
682 | 2 | 12 | 2008 | Ontario, United States | United States | Energy | Plant | GINNA | Single | ? |  | 1 | NA | Inadequate preventative maintenance on the turbine-driven auxiliary feedwater pump governor results in pump failure. | PWR | Operational | 608 | 1969 |  | 0 | Auxiliary feedwater pump (AFW/EFW) | 1 | Inadequate maintenance | H | 0 | 1
683 | 2 | 7 | 2009 | Ontario, United States | United States | Energy | Plant | GINNA | Single | ? |  | 1 | NA | Corrosion binding of the governor control valve results in the turbine-driven auxiliary feedwater pump failure. | PWR | Operational | 608 | 1969 |  | 0 | Auxiliary feedwater pump (AFW/EFW) | 1 | Inadequate maintenance | H | 0 | 0
684 | 4 | 10 | 2013 | Ontario, United States | United States | Energy | Plant | GINNA | Single | ? |  | 1 to 2 | NA | Unanalyzed Condition for Potential Floodwater Intrusion into Vital Battery Rooms. | PWR | Operational | 608 | 1969 |  | 0 | Natural hazards: external flood | 3 | Inadequate design | H | 0 | 1
685 | 14 | 8 | 2003 | Ontario, United States | United States | Energy | Plant | GINNA | Single | ? |  | 1 | NA | Reactor trip and loss of offsite power occurred as a result of the power blackout in the Northeast United States on August 14, 2003. | PWR | Operational | 608 | 1969 |  | 1 | Offsite power blackout | 3 |  | T | 3 | 10
686 | 24 | 4 | 2003 | Port Gibson, United States | United States | Energy | Plant | GRAND GULF | 1 | ? |  | 1 | NA | Plant-centered LOOP and subsequent loss of the instrument air system. | BWR | Operational | 1500 | 1984 |  | 1 | Natural hazards: thunderstor & high wind | 3 |  | T | 15 | 19
687 | 22 | 2 | 2010 | Hartsville, United States | United States | Energy | Plant | ROBINSON | 2 | ? |  | 1 | NA | Concurrent unavailabilities- EDG B inoperable due to failed output breaker and EDG A unavailable due to testing and maintenance. | PWR | Operational | 780 | 1970 |  | 1 | EDG | 1 | vendor workmanship error | H | 0 | 1
689 | 1 | 8 | 1996 | Haddam Neck, United States | United States | Energy | Plant | HADDAM NECK | Single | ? |  | 2 | NA | Potentially inadequate RHR pump net positive suction head following a large- or medium-break LOCA because of design errors. | PWR | Permanent Shutdown | 603 | 1967 |  | 1 | RHR | 1 | Design error | H | 0 | 0
690 | 26 | 6 | 2000 | New Hill, United States | United States | Energy | Plant | HARRIS | 1 | ? |  | 1 | NA | Degraded fire barriers and inadequate fire brigade practice for switchgear room B. | PWR | Operational | 960 | 1987 |  | 1 | Event at auxiliary building: fire | 3 | inadequate design & procedure | H | 1 | 10
691 | 15 | 5 | 1999 | New Hill, United States | United States | Energy | Plant | HARRIS | 1 | ? |  | 1 | NA | Charging/SI Pump “C” inoperable for a time in excess of the TS LCO action statement requirements. | PWR | Operational | 960 | 1987 |  | 1 | Charging Safety Injection Pump (CSIP) | 1 |  | T | 0 | 1
692 | 8 | 10 | 2001 | New Hill, United States | United States | Energy | Plant | HARRIS | 1 | ? |  | 1 | NA | Debris accumulated in suction lines to the A residual heat removal (RHR) pump and a containment spray pump. | PWR | Operational | 960 | 1987 |  | 1 | RHR, containment spray | 1 | Work Practices; Workmanship, substandard cleanliness | H | 0 | 0
694 | 12 | 7 | 2008 | Baxley, United States | United States | Energy | Plant | HATCH | 1,2 | ? |  | 1 | NA | Degraded coupling leads to emergency diesel generator inoperability. | BWR | Operational | 911;921 | 1974;1978 |  | 0 | EDG | 1 | Inadequate maintenance | H | 0 | 1
695 | 15 | 5 | 1985 | Baxley, United States | United States | Energy | Plant | HATCH | 1 | ? |  | 2 | NA | Heating, ventilation, and air conditioning (HVAC) water shorts panel; safety relief valve (SRV) fails open; HPCI fails; reactor core isolation cooling (RCIC) unavailable Water from an HVAC vent fell onto an analog transmitter trip system panel in the control room (the water was from the control room HVAC filter deluge system which had been inadvertently activated as a result of unrelated maintenance activities). This resulted in the lifting of the SRV four times. The SRV stuck open on the fourth cycle, initiating a transient. Moisture also energized the HPCI trip solenoid making HPCI inoperable. RCIC was unavailable due to maintenance. | BWR | Operational | 911 | 1974 |  | 1 |  | 1 |  | T | 3 | 5
697 | 3 | 6 | 1979 | Baxley, United States | United States | Energy | Plant | HATCH | 2 | 1 |  | 2 | NA | During a power increase, the reactor tripped due to a condensate system trip. HPCI failed to initiate on low-low level due to a failed turbine stop valve. In addition, water from leaking mechanical seal lines and an unknown valve caused water to back up and contaminate the pump oil. RCIC was out of service for unspecified reasons. | BWR | Operational | 921 | 1978 |  | 1 | HPCI, condensate system | 1,2 |  | ?
698 | 10 | 10 | 2004 | Salem, United States | United States | Energy | Plant | HOPE CREEK | 1 | ? |  | 1 | NA | Manual reactor scram due to moisture separator reheater drain line failure. | BWR | Operational | 1240 | 1986 |  | 1 | Turbine buidling | 2 |  | T | 20 | 30
699 | 1 | 7 | 2003 | Salem, United States | United States | Energy | Plant | HOPE CREEK | 1 | ? |  | 1 | NA | Station service water Train "A" traveling screen failed due to inadequate maintenance instructions. | BWR | Operational | 1240 | 1986 |  | 1 | station service water system (SSWS) | 2 | Improper maintenance | H | 0 | 0
700 | 27 | 4 | 2005 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 2 | ? |  | 1 | NA | Potential degradation of safety injection system due to nitrogen accumulation from leaking accumulator. | PWR | Operational | 1067 | 1973 |  | 1 | Emergency Core Cooling System (ECCS) | 1 | Inadequate maintenance | H | 0 | 1
701 | 14 | 8 | 2003 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 2,3 | ? |  | 2 | NA | Reactor trip and loss of offsite power occurred as a result of the power blackout in the Northeast United States on August 14, 2003. | PWR | Operational | 1067;1085 | 1973;1976 |  | 1 | Offsite power blackout | 3 |  | T | 3 | 5
703 | 31 | 8 | 1999 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 2 | ? |  | 1 | NA | Loss of offsite power to safety-related buses following a reactor trip and an emergency diesel output breaker trip. | PWR | Operational | 1067 | 1973 |  | 1 |  | 1 |  | T? | 68.12 | 86.12
704 | 5 | 10 | 2005 | Carlton, United States | United States | Energy | Plant | KEWAUNEE | Single | ? |  | 2 | NA | Design deficiency could cause unavailability of safety-related equipment during postulated internal flooding. | PWR | Permanent Shutdown | 595 | 1974 |  | 1 |  | 1 | inadequate design control | H | 0 | 10
705 | 17 | 8 | 2006 | Carlton, United States | United States | Energy | Plant | KEWAUNEE | Single | ? |  | 1 to 2 | NA | Degraded EDG caused by fuel oil leak. | PWR | Permanent Shutdown | 595 | 1974 |  | 1 | EDG | 1 | Inadequate maintenance | H | 0 | 0
706 | 30 | 10 | 2002 | Carlton, United States | United States | Energy | Plant | KEWAUNEE | Single | ? |  | 2 | NA | Potentially unavailable safety-related equipment due to lack of fixed fire suppression system. | PWR | Permanent Shutdown | 595 | 1974 |  | 1 | a fire area where alternative or dedicated shutdown capability was provided | 1? | Inadquate design | H | 0 | 1
708 | 26 | 2 | 2003 | Carlton, United States | United States | Energy | Plant | KEWAUNEE | Single | ? |  | 1 | NA | Concurrent unavailabilities EDG B inoperable due to faulty relay and EDG A out for test and maintenance. | PWR | Permanent Shutdown | 595 | 1974 |  | 1 | EDG | 1 |  | T | 0.8 | 1
710 | 11 | 5 | 1975 | Carlton, United States | United States | Energy | Plant | KEWAUNEE | Single | ? |  | 2 | NA | Inoperable AFW pumps during startup as a result of leaks from the demineralizer into the condensate storage tank (CST) Mixed bed resin beads were leaking from the demineralizer in the makeupwater system and migrated to the CST. As a result, during startup, both motor-driven AFW pump suction strainers became clogged, thereby resulting in low pump flow. The same condition occurred for the turbine-driven AFW pump suction strainer. | PWR | Permanent Shutdown | 595 | 1974 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 |  | ?
711 | 2 | 2 | 2005 | Marseilles, United States | United States | Energy | Plant | LASALLE | 1,2 | ? |  | 1 to 2 | NA | Single-failure vulnerability of 4160 V ESF bus protective relay schemes caused by common power metering circuits. | BWR | Operational | 1207 | 1982;1984 |  | 1 | safety related buses | 1 | inadequate design review | H | 1 | 10
713 | 21 | 9 | 1984 | Marseilles, United States | United States | Energy | Plant | LASALLE | 1 | ? |  | 2 | NA | Operator error causes scram; RCIC unavailable; RHR unavailable. While at 23-percent power, an operator error caused a reactor scram and MSIV closure. RCIC was found to be unavailable during testing (one RCIC pump was isolated and the other pump tripped during the test). RHR was found to be unavailable during testing due to an inboard suction isolation valve failing to open on demand. Both RHR and RCIC may have been unavailable after the reactor scram. | BWR | Operational | 1207 | 1982 |  | 1 | Reactor Core Isolation Cooling (RCIC) | 1 | dirty and/or contaminated lubrication oil | T | 1 | 5
714 | 28 | 6 | 1996 | Marseilles, United States | United States | Energy | Plant | LASALLE | 1,2 | ? |  | 1 | NA | Fouling of the cooling water systems due to concrete sealant injected into the service water tunnel | BWR | Operational | 1207 | 1982;1984 |  | 1 | Service water tunnel: source for the Essential Service Water System, Non-essential Service Water Systems and the Fire Protection systems | 1 | Inadequate work control | H | 40 | 60
716 | 3 | 9 | 2001 | Marseilles, United States | United States | Energy | Plant | LASALLE | 2 | ? |  | 1 | NA | Reactor scram, loss of offsite power to vital bus (blown fuses), and subsequent unavailabilities: core spray pump, residual heat removal pump, and control rod drive pump. | BWR | Operational | 1207 | 1984 |  | 1 | Division 1 undervoltage (UV) protective circuit | 1 | failec fuses | T | 8 | 10
717 | 23 | 4 | 2011 | Limerick, United States | United States | Energy | Plant | LIMERICK | 2 | ? |  | 1 | NA | Reactor core isolation cooling (RCIC) inoperable because of main feedwater valve failures diverting RCIC flow to the main condenser. | BWR | Operational | 1194 | 1989 |  | 0 | primary containment isolation valve (PCIV), core isolation cooling system (RCIC) | 1 | Inadequate procedure | H | 0 | 0
718 | 23 | 2 | 2001 | Limerick, United States | United States | Energy | Plant | LIMERICK | 2 | ? |  | 1 | NA | Inadvertent opening/stuck open main steam relief valve(MSRV). | BWR | Operational | 1194 | 1989 |  | 1 | Main Steam Relief Valve (MSRV) | 2 | erosion and oxidation | T | 8 | 11
719 | 6 | 8 | 2007 | Cornelius, United States | United States | Energy | Plant | MCGUIRE | 1,2 | ? |  | 1 | NA | Potential inoperability of service water strainer backwash system during accident conditions. | PWR | Operational | 1215 | 1981;1983 |  | 0 | Nuclear Service Water (RN) System | 1? | deficient procedure guidance | H | 1 | 10
720 | 12 | 2 | 2011 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 2 | ? |  | 1 to 2 | NA | Inadequate procedures and operator errors caused unplanned reactivity additions during main turbine control valve testing. | PWR | Operational | 918 | 1975 |  | 1 |  | 1 | deficient procedure guidance | H | 0 | 0
721 | 20 | 9 | 2000 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 2 | ? |  | 1 | NA | Failure of turbine-driven auxiliary feedwater pump during testing. | PWR | Operational | 918 | 1975 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 | Inadequate maintenance | H | 0 | 1
722 | 23 | 2 | 2006 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 2 | ? |  | 1 | NA | Reactor trip caused by loss of instrument air. | PWR | Operational | 918 | 1975 |  | 1 | Turbine buidling | 2 |  | T | 6 | 7
724 | 20 | 7 | 1976 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 2 | ? |  | 3 | NA | With the reactor at power, a main circulating water pump was started, and this resulted in an in-plant voltage reduction to below the revised trip set point. This isolated the safety-related buses and started the EDGs. Each time a major load was tied onto the diesel, the revised under-voltage trip set points tripped the load. As a result, at the end of the EDG loading sequence, all major loads were isolated even though the EDGs were tied to the safety-related buses. | PWR | Operational | 918 | 1975 | <LC> ref/source missing | 1
725 | 2 | 1 | 1981 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 2 | ? |  | 2 | NA | When the reactor was at full power, the 125v DC emergency bus was lost as a result of operator error. The loss of the bus caused the reactor to trip, but the turbine failed to trip because of the unavailability of DC bus "A" Loads were not switched to the reserve transformer (following the manual turbine trip) because of the loss of DC bus "A". Two breakers (on the "B" 6.9kV and 4.16kV buses) remained open, thereby causing a LOOP. EDG "B" tripped as a result of leakage of the service water (SW) flange, which also caused the "B" 4.16 kV bus to be deenergized. An operator recognition error caused the PORV to be opened at 2380 psia. | PWR | Operational | 918 | 1975 |  | 1 |  | 1 |  | H | 1 | 10
726 | 11 | 8 | 2013 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 3 | ? |  | 1 | NA | Turbine Driven Auxiliary Feedwater Pump Operability Impacted by Incorrect Bearing. | PWR | Operational | 1280 | 1986 |  | 0 | Auxiliary feedwater pump (AFW/EFW) | 1 | Inadequate inspection & maintenance | H | 0 | 1
728 | 29 | 2 | 2012 | Monticello, United States | United States | Energy | Plant | MONTICELLO | Single | ? |  | 1 to 2 | NA | Failure to maintain flood plan to protect the site against external flooding events. | BWR | Operational | 691 | 1971 |  | 1 | Natural hazards: external flood | 3 | Inadequate design | H | 0 | 0
729 | 7 | 3 | 2003 | Scriba, United States | United States | Energy | Plant | NINE MILE POINT | 1 | ? |  | 1 | NA | Potential unavailability of reactor building closed loop cooling system due to degraded piping. | BWR | Operational | 642 | 1969 |  | 1 | reactor building closed loop cooling (RBCLC) | 1 | Inadequate design, inspection, maintenance | H | 0 | 0
730 | 14 | 8 | 2003 | Scriba, United States | United States | Energy | Plant | NINE MILE POINT | 1,2 | ? |  | 1 | NA | Grid-related LOOP due to August 14, 2003 Northeast Blackout. | BWR | Operational | 642;1320 | 1969;1987 |  | 1 | Offsite power blackout | 3 |  | T | 14 | 18
734 | 13 | 11 | 2001 | Mineral, United States | United States | Energy | Plant | NORTH ANNA | 2 |  |  |  | NA | RPV head leakage due to PWSCC of one CRDM nozzle. | PWR | Operational | 1011 | 1980 |  | 1 | RPV head | 1 | PWSCC | T | 80 | 150
736 | 28 | 4 | 2006 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 1 | NA | Failure to maintain design control for an SSF flooding boundary. | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 0 | Standby Shutdown Facility (SSF) | 1 | Inadequate maintenance procedure | H | 0 | 0
737 | 15 | 4 | 2008 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 1 | NA | Procedure error leads to loss of reactor coolant system inventory while shutdown. | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 0 | Main generator | 2 | Inadequate maintenance procedure | H | 10 | 100
740 | 11 | 11 | 2013 | Oconee, United States | United States | Energy | Plant | OCONEE | 1 | ? |  | 1 to 2 | NA | High Cycle Fatigue Resulted in Reactor Coolant Leak and Unit Shutdown. | PWR | Operational | 891 | 1973 |  | 1 | High Pressure Injection (HPI) | 1 | Inadequate inspection & maintenance | H | 30 | 50
741 | 30 | 4 | 2001 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 1 to 2 | NA | Potential unavailability of high pressure injection (HPI) and component cooling water (CCW) pumps due to flooding caused by a postulated break on non-seismically qualified piping. | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 1 | Natural hazard: seismic | 3 | Inadequate design | H | 0 | 0
742 | 4 | 12 | 2000 | Oconee, United States | United States | Energy | Plant | OCONEE | 1 |  |  |  | NA | RPV head leakage resulted from primary water stress corrosion cracking(PWSCC) of one CRDM nozzle. | PWR | Operational | 891 | 1973 |  | 1 | RPV head | 1 | PWSCC | T | 5 | 15
743 | 24 | 2 | 1999 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 1 to 2 | NA | Postulated high-energy line leaks or breaks in turbine building leading to failure of safety-related 4 kV switch gear. | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 1 | Turbine buidling | 2 |  | H? | 0 | 0
745 | 19 | 6 | 2000 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 1 | NA | Non-seismic 16-inch fire system piping header transited through the auxiliary building and posed a potential flooding problem if the piping ruptured during a seismic event. | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 1 | Natural hazard: seismic | 3 | Inadequate design, inspection, maintenance | H | 0 | 0
748 |  |  | 1998 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 1 | NA | Incorrect calibration of the borated water storage tank (BWST) level instruments resulted in a situation where the emergency operating procedure (EOP) requirements for BWST-to-reactor building emergency sump transfer would never have been met; operators would be working outside the EOP | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 1 | Emergency Core Cooling System (ECCS) | 1 | Deficient Written Documentation, technical inaccuracy | H | 0 | 0
751 | 20 | 2 | 2010 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 1 to 2 | NA | Standby shutdown facility reactor coolant make-up system letdown line orifice strainer blocked by valve gasket. | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 1 | Standby Shutdown Facility (SSF) Reactor Coolant Make-Up (RCMU) system | 1 |  | T;H | 5 | 10
752 | 11 | 8 | 2011 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 2 | NA | Failure to maintain design control of the SSF pressurizer heater breakers. | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 1 | Standby Shutdown Facility pressurizer (PZR) | 1 | Inadequate design | H | 0 | 1
755 | 28 | 4 | 2001 | Oconee, United States | United States | Energy | Plant | OCONEE | 2 |  |  |  | NA | RPV head leakage due to PWSCC of four CRDM nozzles. | PWR | Operational | 891 | 1973 |  | 1 | RPV head | 1 | PWSCC | T | 50 | 150
757 | 1 | 5 | 2006 | Oconee, United States | United States | Energy | Plant | OCONEE | 3 | ? |  | 1 | NA | Potentially degraded containment sump recirculation because of debris. | PWR | Operational | 900 | 1974 |  | 0 | reactor building emergency sump suction lines | 1 | Inadequate procedure | H | 0 | 0
760 | 30 | 5 | 2002 | Oconee, United States | United States | Energy | Plant | OCONEE | 3 | ? |  | 1 | NA | Potential unavailability of a HPI pump due to improperly installed wire connectors during a postulated severe LOOP or high energy line break (HELB). | PWR | Operational | 900 | 1974 |  | 1 | high pressure injection (HPI) pump | 1 | Improper maintenance | H | 0 | 0
763 | 18 | 2 | 2001 | Oconee, United States | United States | Energy | Plant | OCONEE | 3 |  |  |  | NA | RPV head leakage due to PWSCC of nine CRDM nozzles. | PWR | Operational | 900 | 1974 |  | 1 | RPV head | 1 | PWSCC | T | 100 | 200
764 |  |  | 2000 | Oconee, United States | United States | Energy | Plant | OCONEE | 1,2,3 | ? |  | 1 to 2 | NA | Potential inoperability of a HPI pump following a tornado of F3, F4, or F5 severity. | PWR | Operational | 891;891;900 | 1973;1973;1974 |  | 1 | Natural hazard: tornado | 3 | Inadequate procedure | H | 0 | 1
766 |  |  | 2014 | Forked River, United States | United States | Energy | Plant | OYSTER CREEK | Single | ? |  | 2 | NA | Technical Specification Prohibited Condition Causedby Two Electromagnetic Relief Valves Inoperable for Greater Than Allowed Outage Time. | BWR | Operational | 652 | 1969 |  | 1 | Electromagnetic relief valves (EMRVs) | 1 | inadequate design & procedure | H | 4 | 7
767 | 12 | 9 | 2014 | Forked River, United States | United States | Energy | Plant | OYSTER CREEK | Single | ? |  | 1 to 2 | NA | Technical Specification Prohibited Condition Caused by Emergency Diesel Generator Inoperable for greater than allowed outage time. | BWR | Operational | 652 | 1969 |  | 1 | EDG | 1 |  | T;H | 0 | 1
768 | 20 | 5 | 2003 | Forked River, United States | United States | Energy | Plant | OYSTER CREEK | Single | ? |  | 1 | NA | Loss of 4.16kV Emergency Bus 1C due to ground fault in normally energized underground cable. | BWR | Operational | 652 | 1969 |  | 1 | Power supply: 4160 VAC bus 1C | 2? | cable degradation | T | 9 | 11
769 | 2 | 5 | 1979 | Forked River, United States | United States | Energy | Plant | OYSTER CREEK | Single | ? |  | 2 | NA | While testing the isolation condenser, a reactor scram occurred. The feedwater pump tripped and failed to restart. The recirculation pump inlet valves were closed. The isolation condenser was used during cooldown. | BWR | Operational | 652 | 1969 |  | 1 | Isolation condenser | 1 |  | ? | 1 | 10
770 | 17 | 10 | 2010 | South Haven, United States | United States | Energy | Plant | PALISADES | Single | ? |  | 1 | NA | Turbine-driven AFW pump unavailable because of greasing of the wrong component in the pump. | PWR | Operational | 850 | 1971 |  | 0 | Auxiliary feedwater pump (AFW/EFW) | 1 | Improper maintenance | H | 0 | 0
771 | 21 | 6 | 2001 | South Haven, United States | United States | Energy | Plant | PALISADES | Single | ? |  | 1 | NA | RPV head leakage due to PWSCC of one CRDM nozzle | PWR | Operational | 850 | 1971 |  | 1 | RPV head | 1 | PWSCC | T | 280 | 350
772 | 11 | 9 | 2001 | South Haven, United States | United States | Energy | Plant | PALISADES | Single | ? |  | 1 | NA | Smoke detectors in the cable room were not installed in accordance with code. | PWR | Operational | 850 | 1971 |  | 1 | Event at auxiliary building: (potential) fire in cable spreading room | 3? | Inadequate design | H | 0 | 0
773 | 25 | 3 | 2003 | South Haven, United States | United States | Energy | Plant | PALISADES | Single | ? |  | 1 | NA | Plant-centered LOOP (Mode 6) and temporary loss of shutdown cooling. | PWR | Operational | 850 | 1971 |  | 1 | Power supply: control power cable associated with offsite power feeds | 2 | deficient procedure guidance | H | 0 | 1
775 | 31 | 7 | 2004 | Wintersburg, United States | United States | Energy | Plant | PALO VERDE | 1,2,3 | ? |  | 2 | NA | Containment sump recirculation potentially inoperable due to pipe voids. | PWR | Operational | 1414 | 1985;1986;1987 |  | 1 | Emergency Core Cooling System (ECCS) | 1 | Inadequate procedure | H | 1 | 10
776 | 19 | 2 | 2004 | Wintersburg, United States | United States | Energy | Plant | PALO VERDE | 2 | ? |  | 1 | NA | Failure to implement design of steam generator nozzle dam requiring an extended time in reduced RCS inventory configuration. | PWR | Operational | 1414 | 1986 |  | 1 | Steam generator | 2 | Improper maintenance | H | 0 | 0
779 | 25 | 7 | 2006 | Wintersburg, United States | United States | Energy | Plant | PALO VERDE | 3 | ? |  | 1 | NA | Inoperable EDG caused by inadequate maintenance procedures and corrective actions. | PWR | Operational | 1414 | 1987 |  | 0 | EDG | 1 | Inadequate procedure & maintenance | H | 0 | 0
781 | 17 | 3 | 2004 | York County, United States | United States | Energy | Plant | PEACH BOTTOM | 3 | ? |  | 1 | NA | High-pressure coolant injection (HPCI) unavailable due to failed flow controller. | BWR | Operational | 1412 | 1974 |  | 1 | High Pressure Coolant Injection (HPCI) | 1 | Failed flow controller | T | 0 | 1
782 | 14 | 8 | 2003 | Perry, United States | United States | Energy | Plant | PERRY | 1 | ? |  | 1 | NA | Grid-related LOOP due to August 14, 2003 Northeast Blackout. | BWR | Operational | 1303 | 1986 |  | 1 | offsite power blackout | 3 |  | T | 15 | 19
783 | 5 | 9 | 2003 | Perry, United States | United States | Energy | Plant | PERRY | 1 | ? |  | 1 | NA | ESW pump A failure to run due to shaft failure and inadequate repairs led to a second failure. | BWR | Operational | 1303 | 1986 |  | 1 | Emergency service water system (ESWS) | 1 | stress corrosion cracking (SCC); inadequate procedure | T;H | 5 | 20
784 | 10 | 5 | 2011 | Plymouth, United States | United States | Energy | Plant | PILGRIM | 1 | ? |  | 1 | NA | Failure to effectively implement operations and reactivity control standards and procedures during a reactor startup caused an unrecognized subcriticality and return to criticality with a subsequent reactor scram. | BWR | Operational | 711 | 1972 |  | 0 | Reactor | 1 | operational deficiencies | H | 0 | 0
785 | 8 | 2 | 2013 | Plymouth, United States | United States | Energy | Plant | PILGRIM | 1 | ? |  | 1 | NA | LOOP events due to Winter Storm Nemo. | BWR | Operational | 711 | 1972 |  | 1 | Natural hazard: storm | 3 |  | T | 7 | 13
786 | 14 | 10 | 2013 | Plymouth, United States | United States | Energy | Plant | PILGRIM | 1 | ? |  | 1 | NA | LOOP and Reactor Scram. | BWR | Operational | 711 | 1972 |  | 1 | Offsite substatio | 3 |  | T | 8 | 15
787 | 21 | 5 | 2012 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1 | ? |  | 0 to 1 | NA | Inadequate maintenance leads to failure of turbine-driven auxiliary feedwater pump. | PWR | Operational | 640 | 1970 |  | 0 | Auxiliary feedwater pump (AFW/EFW) | 1 | Inadequate maintenance procedure | H | 0 | 1
788 | 13 | 3 | 2013 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1,2 | ? |  | 1 to 2 | NA | Flooding procedure failed to protect safety-related equipment. | PWR | Operational | 640 | 1970;1972 |  | 1 | Natural hazards: external flood | 3 | Inadequate design | H | 0 | 10
789 | 29 | 10 | 2002 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1,2 | ? |  | 1 to 2 | NA | Potential common-mode failure of all EFW pumps due to clogging of recirculation lines during switch over to service water. | PWR | Operational | 640 | 1970;1972 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 | Inadequate design | H | 0 | 1
790 | 8 | 11 | 2005 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1,2 | ? |  |  | NA | Calculation errors could lead to degraded long-term ECCS cooling. | PWR | Operational | 640 | 1970;1972 |  | 1 | Emergency Core Cooling System (ECCS) | 1 | incorrect design calculation settings | H | 0 | 1
791 | 12 | 1 | 1971 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1 | ? |  | 2 | NA | ? During a routine check of the containment tendon access gal [DESCRIPTION INCOMPLETE] | PWR | Operational | 640 | 1970 | <LC> incomplete description | 1
792 | 7 | 4 | 1974 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1 | ? |  | 2 | NA | Inoperable EFW pumps during shutdown while the reactor was in cooldown mode, motor-driven EFW pump A did not provide adequate flow. The operators were unaware that the in-line suction strainers were 95 percent plugged (both motor-driven pumps A and B). Apartially plugged strainer was found in each of the suction lines for both turbine-driven EFW pumps. | PWR | Operational | 640 | 1970 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 |  | ?
794 | 15 | 1 | 2008 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1 | ? |  | 1 | NA | Concurrent unavailabilities- station auxiliary transformer and 480V safety bus. | PWR | Operational | 640 | 1970 |  | 1 | Power supply: 480 Vac safeguards bus, station auxiliary transformer | 1,2 | Inadequate design, test, maintenance | H | 18 | 30
796 | 29 | 11 | 2001 | Two Creeks, United States | United States | Energy | Plant | POINT BEACH | 1,2 | ? |  | 2 to 3 | NA | Potential common-mode failure of all AFW pumps. | PWR | Operational | 640 | 1970;1972 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 | misalignment between plant design and plant procedures | H | 0 | 0
797 | 31 | 7 | 2008 | Red Wing, United States | United States | Energy | Plant | PRAIRIE ISLAND | 1 | ? |  | 0 to 1 | NA | Turbine-driven auxiliary feedwater pump inoperable due to valve out-of-position. | PWR | Operational | 566 | 1973 |  | 0 | Auxiliary feedwater pump (AFW/EFW) | 1 | Inadequate inspection & maintenance | H | 2 | 4
798 | 22 | 10 | 2010 | Red Wing, United States | United States | Energy | Plant | PRAIRIE ISLAND | 1 | ? |  | 1 to 2 | NA | Battery chargers potentially inoperable because of an under-voltage condition. | PWR | Operational | 566 | 1973 |  | 1 | Power supply: safety-related battery chargers | 1 | Inadequate design | H | 0 | 0
799 | 1 | 11 | 2000 | Red Wing, United States | United States | Energy | Plant | PRAIRIE ISLAND | 1,2 | ? |  | 1 | NA | Potential unavailability of service water (SW) pumps due to improper design modification of backflush system and failure of vacuum valves. | PWR | Operational | 566;560 | 1973;1974 |  | 1 | Essential Service Water (ESW) system | 1 | inadequate design review | H | 1 | 10
800 | 28 | 7 | 2008 | Red Wing, United States | United States | Energy | Plant | PRAIRIE ISLAND | 2 | ? |  | 1 to 2 | NA | Potential unavailability of the component cooling water system during a postulated high-energy linebreak due to inadequate design. | PWR | Operational | 560 | 1974 |  | 1 | Component cooling water (CCW) system | 2 | inadequate design control | H | 2 | 3
802 |  | 11 | 2002 | Cordova, United States | United States | Energy | Plant | QUAD CITIES | 1 | ? |  | 0 to 1 | NA | ERVs were inoperable during extended power uprateconditions because of inadequate power uprate evaluation. | BWR | Operational | 940 | 1972 |  | 0 | electromatic relief valve (ERV) | 1 | inadequate design control | H | 8 | 12
803 | 2 | 8 | 2001 | Cordova, United States | United States | Energy | Plant | QUAD CITIES | 1,2 | ? |  | 1 | NA | Reactor scram attributable to failure of main power transformer. | BWR | Operational | 940 | 1972 |  | 1 | Natural hazards: lightning | 3 |  | T | 35 | 50
805 | 19 | 10 | 2006 | St. Francisville, United States | United States | Energy | Plant | RIVER BEND | 1 | ? |  | 1 | NA | Automatic reactor scram due to inadvertent isolation of main feedwater. | BWR | Operational | 1016 | 1985 |  | 1 | Main Feedwater header | 2 |  | T | 6 | 8
806 | 24 | 5 | 2012 | St. Francisville, United States | United States | Energy | Plant | RIVER BEND | 1 | ? |  | 2 | NA | Loss of normal service water, circulating water, and feedwater caused by electrical fault. | BWR | Operational | 1016 | 1985 |  | 1 | Main Reactor Feedwater Pump | 2 |  | T | 16 | 20
807 | 10 | 12 | 2004 | St. Francisville, United States | United States | Energy | Plant | RIVER BEND | 1 | ? |  | 1 | NA | Reactor trip due to loss of a non-vital 120V instrument bus. | BWR | Operational | 1016 | 1985 |  | 1 | Power supply: non-safety related instrument bus | 2 | failed circuit board | T | 5 | 10
808 | 2 | 10 | 2012 | Hartsville, United States | United States | Energy | Plant | ROBINSON | 2 | ? |  | 0 to 1 | NA | Failure of dedicated shutdown diesel generator. | PWR | Operational | 780 | 1970 |  | 0 | dedicated shutdown diesel generator (DSDG) | 1 | Inadequate inspection & maintenance | H | 0 | 1
809 | 27 | 11 | 1978 | Salem, United States | United States | Energy | Plant | SALEM | 1 | ? |  | 3 | NA | Loss of vital bus and scram; multiple components lost. While the reactor was at 100-percent power, vital instrument bus B was lost as a result of the failure of an output transformer and two regulating resistors. Loss of the vital bus caused a false low RCS loop flow signal, thereby causing a reactor trip. Two AFW pumps failed to start (one because of the loss of vital bus B, and the other because of a maladjustment of the over-speed trip mechanism). Inadvertent safety injection occurred as a result of decreasing average coolant temperature and safety injection signals. | PWR | Operational | 1254 | 1976 |  | 1 | Power supply: vital instrument bus, AFW | 1 |  | ?
811 | 28 | 10 | 1999 | Salem, United States | United States | Energy | Plant | SALEM | 1,2 | ? |  | 1 | NA | Degraded CO2 fire suppression system in the 4160Vac switchgear room. | PWR | Operational | 1254;1200 | 1976;1981 |  | 1 | Event at auxiliary building: (potential) fire in switchgear room | 3 | Human error | H | 0 | 0
812 | 25 | 3 | 2008 | San Clemente, United States | United States | Energy | Plant | SAN ONOFRE | 2 | ? |  | 0 to 1 | NA | Deficient electrical connections with potential to affect multiple safety systems. | PWR | Permanent Shutdown | 1127 | 1982 |  | 1 | Power supply: safety-related 125 Vdc station battery Breaker | 1 | deficient procedure guidance | H | 0 | 0
816 | 15 | 12 | 2012 | Daisy, United States | United States | Energy | Plant | SEQUOYAH | 1,2 | ? |  | 2 | NA | Inadequate electrical conduit seals for the Essential Raw Cooling Water Pumping Station could result in loss of diesel generators during a flooding event. | PWR | Operational | 1221;1200 | 1980;1981 |  | 1 | Natural hazards: external flood | 3 | Inadequate design | H | 30 | 40
819 | 18 | 1 | 2014 | New Hill, United States | United States | Energy | Plant | HARRIS | 1 | ? |  | 1 | NA | Manual reactor trip due to indications of a fire. | PWR | Operational | 960 | 1987 |  | 1 | Power supply: 480 Vac safeguards bus, station auxiliary transformer | 1,2 |  | T | 7 | 15
821 | 18 | 12 | 2001 | New Hill, United States | United States | Energy | Plant | HARRIS | 1 | ? |  | 1 to 2 | NA | Degraded fire barrier and lack of fire brigade training could cause unavailability of Train B safety equipment and TDAFW pump flow control. | PWR | Operational | 960 | 1987 |  | 1 | Event at auxiliary building: inadequate fire barrier assembly between the B Train Switchgear Room/Auxiliary Control Panel Room and the A Train Cable Spreading Room | 3 | Inadequate design | H | 0 | 0
822 | 20 | 12 | 2002 | New Hill, United States | United States | Energy | Plant | HARRIS | 1 | ? |  | 1 | NA | Postulated fire could cause the actuation of certain valves that could result in a loss of the charging pump, RCP seal cooling, loss of RCS inventory, and other conditions. | PWR | Operational | 960 | 1987 |  | 1 | Charging/Safety Injection Pump (CSIP), Reactor Coolant Pump (RCP) | 1 | inadequate Safe Shutdown Analysis | H | 0 | 1
823 | 16 | 10 | 2008 | Fort Pierce, United States | United States | Energy | Plant | ST. LUCIE | 1 | ? |  | 2 to 3 | NA | Air intrusion into component cooling water system causes pump cavitation. | PWR | Operational | 1045 | 1976 |  | 1 | Component cooling water (CCW) system | 2 | Inadequate maintenance | H | 0 | 1
824 | 9 | 1 | 2014 | Fort Pierce, United States | United States | Energy | Plant | ST. LUCIE | 1 | ? |  | 1 to 2 | NA | Internal Reactor Auxiliary Building Flooding During Heavy Rain Due to Degraded Conduits Lacking Internal Flood Barriers. | PWR | Operational | 1045 | 1976 |  | 1 | Natural hazards: flooding | 3 | Inadequate design | H | 0 | 10
825 | 25 | 9 | 2004 | Fort Pierce, United States | United States | Energy | Plant | ST. LUCIE | 1,2 | ? |  | 1 | NA | Severe weather LOOP caused by Hurricane Jeanne while the plant was shutdown. | PWR | Operational | 1045;1050 | 1976;1983 |  | 1 | Natural hazards: hurricane | 3 |  | T | 25 | 40
826 | 11 | 6 | 1980 | Fort Pierce, United States | United States | Energy | Plant | ST. LUCIE | 1 | ? |  | 2 | NA | At 100% power, a moisture-induced short circuit in a solenoid valve caused a CCW containment isolation valve to shut causing loss of CCW to all reactor coolant pumps(RCPs). While reducing pressure to initiate the shutdown cooling system (SCS), the top head water flashed to steam, thus forming a bubble (initially undetected by the operators). During the cooldown, the SCS relief valves lifted and low-pressure safety injection (LPSI) initiated (i.e.,the other LPSI pump started charging, while the other wasused for cooldown). | PWR | Operational | 1045 | 1976 |  | 1 | Component cooling water (CCW) system | 2 |  | T | 0 | 10
827 | 30 | 4 | 2003 | Fort Pierce, United States | United States | Energy | Plant | ST. LUCIE | 2 | ? |  | 1 | NA | Reactor pressure vessel head leakage because of cracking of control rod drive mechanism nozzles. | PWR | Operational | 1050 | 1983 |  | 1 | RPV head | 1 | PWSCC | T | 1 | 10
828 | 21 | 9 | 2000 | Jenkinsville, United States | United States | Energy | Plant | SUMMER | 1 | ? |  | 1 | NA | Discharge valve to turbine-driven auxiliary feedwater pump locked closed for 48days. | PWR | Operational | 1006 | 1982 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 | Improper maintenance | H | 0 | 0
829 | 23 | 4 | 2001 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 1,2 | ? |  | 1 | NA | EDG 3 is unavailable due to abnormal wear of piston rings. | PWR | Operational | 890 | 1972;1973 |  | 1 | EDG | 1 |  | T | 1 | 10
830 | 28 | 10 | 2001 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 1 |  |  |  | NA | RPV head leakage due to PWSCC of two CRDM nozzles. | PWR | Operational | 890 | 1972 |  | 1 | RPV head | 1 | PWSCC | T | 40 | 80
832 | 16 | 4 | 2011 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 1,2 | ? |  | 2 | NA | Dual unit loss of offsite power because of switchyard damage caused by a tornado. | PWR | Operational | 890 | 1972;1973 |  | 1 | Natural hazard: tornado | 3 |  | T | 20 | 40
834 | 3 | 11 | 2003 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 1 | ? |  | 1 | NA | Potential loss of reactor coolant pump (RCP) seal cooling due to postulated fire damage to emergency switchgear. | PWR | Operational | 890 | 1972 |  | 1 | Emergency Switchgear Room (ESGR) | 1 | Unanalyzed Condition | H | 0 | 1
836 | 7 | 10 | 2006 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 2 | ? |  | 1 | NA | Partial loss of offsite power with subsequent reactor trip. | PWR | Operational | 890 | 1973 |  | 1 | Turbine buidling | 2 |  | T | 30 | 50
837 | 12 | 10 | 2001 | Dauphin, United States | United States | Energy | Plant | THREE MILE ISLAND | 1 | ? |  | 1 | NA | RPV head leakage due to PWSCC of eight thermocouple nozzles and five CRDM nozzles. | PWR | Operational | 880 | 1974 |  | 1 | RPV head | 1 | PWSCC | T | 10 | 25
839 | 7 | 11 | 2005 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3,4 | ? |  | 0 to 1 | NA | AFW pump inoperable for greater time than allowed by technical specifications. | PWR | Operational | 829 | 1972;1973 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 | Inadequate inspection & maintenance | H | 0 | 0
840 | 8 | 3 | 2006 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3 | ? |  | 1 | NA | Loss of RHR while in Mode 5 because of electrical complications. | PWR | Operational | 829 | 1972 |  | 0 | RHR | 1 | Improper maintenance | H | 0 | 0
841 | 8 | 5 | 1974 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3 | ? |  | 3 | NA | Failure of three EFW pumps to start during test. Operators attempted to start all three EFW pumps while the reactor was at power for testing. Two of the pumps failed to start as a result of over-tightened packing. The third pump failed to start because of a malfunction in the turbine regulating valve pneumatic controller. | PWR | Operational | 829 | 1972 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 |  | T;H
842 | 27 | 12 | 1986 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3 | ? |  | 2 | NA | The reactor was tripped manually following a loss ofturbine governor oil system pressure and the subsequent rapid electrical load decrease. Control rods failed to insert automatically because of two cold solder joints in the power mismatch circuit. During the transient, a power-operated relief valve (PORV) opened but failed to close(the block valve had to be closed). The loss of governor oil pressure was due to a cleared orifice blockage and the auxiliary governor dumping control oil. | PWR | Operational | 829 | 1972 |  | 1 | Control rod, PORV; Turbine governer | 1,2 |  | T | 8 | 12
843 | 3 | 2 | 2004 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3,4 | ? |  | 1 to 2 | NA | Triennial fire protection issues. | PWR | Operational | 829 | 1972;1973 |  | 1 | Event at auxiliary building: (potential) fire in mechanical equipment room, control circuits, cables | 3? | inadequate design & procedure | H | 0 | 10
844 | 20 | 11 | 2004 | Waynesboro, United States | United States | Energy | Plant | VOGTLE | 2 | ? |  | 1 | NA | Reactor trip with safety injection and full-open demand from steam bypass valves caused by operator error and failed circuit card. | PWR | Operational | 1229 | 1989 |  | 1 | Instrumentation & Control: solid state protection system (SSPS) | 1 | Failed circuit board, human error | T;H | 5 | 10
845 | 29 | 8 | 2005 | Killona, United States | United States | Energy | Plant | WATERFORD | 3 | ? |  | 1 | NA | Severe weather LOOP caused by Hurricane Katrina while plant was shutdown. | PWR | Operational | 1250 | 1985 |  | 1 | Natural hazards: hurricane | 3 |  | T | 40 | 60
846 | 26 | 5 | 2013 | Killona, United States | United States | Energy | Plant | WATERFORD | 3 | ? |  | 0 to 1 | NA | Emergency diesel generator inoperable due to room exhaust-fan fire. | PWR | Operational | 1250 | 1985 |  | 0 | EDG | 1 | Inadequate procedure | H | 0 | 1
847 | 22 | 11 | 2004 | Spring City, United States | United States | Energy | Plant | WATTS BAR | 1 | ? |  | 1 | NA | Component cooling backup line from essential raw cooling water unavailable due to silt blockage. | PWR | Operational | 1210 | 1996 |  | 1 | essential raw cooling water (ERCW) | 1? | Inadequate maintenance | H | 0 | 0
849 | 13 | 1 | 2012 | Burlington, United States | United States | Energy | Plant | WOLF CREEK | Single | ? |  | 2 | NA | Multiple switchyard faults cause reactor trip and subsequent loss of offsite power. | PWR | Operational | 1285 | 1985 |  | 1 | Switchyard | 2 |  | T | 130 | 200
852 | 17 | 9 | 1994 | Burlington, United States | United States | Energy | Plant | WOLF CREEK | Single | 0 |  | 2 | NA | When the plant was in cold shutdown, operators implemented two unpermitted simultaneous evolutions,which resulted in the transfer of 9,200 gallons of reactor coolant system (RCS) inventory to the reactor water storage tank (RWST). Operators immediately diagnosed the problem and terminated the event by closing the residual heat removal (RHR) cross-connect motor-operated valve (MOV). The temperature of the RCS increased by 7EF as a result of this event. | PWR | Operational | 1285 | 1985 |  | 1 | Reactor Coolant System (RCS) | 1 | Human error | H | 0 | 0
853 | 12 | 7 | 1977 | Zion, United States | United States | Energy | Plant | ZION | 2 | ? |  | 2 | NA | Testing causes instrumentation errors. With the reactor in hot shutdown, testing caused operators to lose indications of reactor and secondary system parameters. In addition, inaccurate inputs were provided to control and protection systems. | PWR | Permanent Shutdown | 1085 | 1973 | <LC> insufficient information | 1 |  |  |  | H
854 | 2 | 11 | 1978 | Ohkuma-Machi, Japan | Japan | Energy | Plant | FUKUSHIMA-DAIICHI | 3 | 0 |  | ? | A | According to TEPCO, during the regular inspection five out of 137 control rods of the reactor came off, possibly triggering a self-sustained nuclear fission reaction. | BWR | Permanent Shutdown | 784 | 1974 | Lack of official information | ? | Control rod | 1 |  | ? | 0 | 0
857 | 24 | 9 | 1990 | Cáceres, Spain | Spain | Energy | Plant | ALMARAZ | 1 or 2? | 0 |  | 1 | WE | Total loss of reactor heat removal (RHR) because of a misalignment of the one RHR train, and unavailability of the other train. This lasted for 46 minutes, and there was a heat-up of the primary coolant from 40 to 70 C. | PWR |  | 1049 or 1044 | 1981 or 1983 | minor safety significance - human (procedural) | 1 |  | 1 |  | H | 0 | 10
858 | 25 | 9 | 1999 | Barseback, Sweden | Sweden | Energy | Plant | BARSEBACK | 2 | 2 | 2 |  | NE | When performing recurrent inspection of the system for auxiliary cooling, eight valves were manually closed by mistake. This caused cooling capacity unavailability during six minutes in the component cooling system which in turn caused safety system unavailability, i.e. containment spray, residual heat removal and diesel generators. Manual scram was initiated and one minute later cooling capacity re-established. | BWR | Permanent Shutdown | 615 | 1977 | INES 2 due insufficient safety system availability | 1 |  | 1 |  | H | 0 | 1
859 | 11 | 6 | 1998 | Léré, France | France | Energy | Plant | BELLEVILLE | 2 | 2 | 2 |  | WE | While the reactor was operating, during a periodic test, a spurious triggering of the containment spray system issued a command to isolate the containment which in turn caused the primary pumps to cut out. This was followed by a reactor emergency shutdown during which one of 65 control clusters remained jammed in the high position.. The operator then applied the relevant incident procedures in order to bring the reactor into a safe state. This incident had no effect on the environment. | PWR | Operational | 1363 | 1988 | INES 2 due to several independent failures affecting safety systems | 1 |  | 1 |  | H | 10 | 200
860 | 6 | 4 | 1996 | Léré, France | France | Energy | Plant | BELLEVILLE | 1 | 2 | 2 |  | WE | A control rod jammed at the top of the core during a scram. The scram was due to an error in the realization of a periodic test of the rods. The incident had no impact on the fuel because the jamming of a control rod is anticipated by the design of the protection system. During following control rod drop tests no anomaly was detected. | PWR | Operational | 1363 | 1987 | INES 2 probably due to degradation of safety function | 1 |  | 1 |  | T | 0 | 10
861 | 22 | 6 | 1991 | Léré, France | France | Energy | Plant | BELLEVILLE | 2 | 0 | 2 |  | WE | During reactor shutdown for partial inspection and refueling, cracks were observed in the small-diameter branch-pipes in the two low-pressure safety injection system circuits; their function of this circuit is in the event of an accident (such as a break in the reactor primary cooling system) to introduce borated water into the vessel in order to stop the nuclear reaction and to provide water for core cooling. The activation of the circuit could have resulted in the cracks (several centimeters long) bursting open and thus jeopardizing the safety of the reactor. However, a preliminary study seems to indicate that the safety margins used in the circuit calculations would have made it possible to bring the reactor to a safe shutdown state. | PWR | Operational | 1363 | 1988 | Level 2 on the French severity scale due to identical (common mode) cracks in two circuits of an important safety system | 1 |  | 1 |  | T | 0 | 10
862 | 24 | 5 | 1991 | Léré, France | France | Energy | Plant | BELLEVILLE | 2 | 0 | 2 |  | WE | While the reactor was shut down for a full inspection and fuel reloading, the pumps of the shutdown cooling system (RRA) showed signs of abnormal functioning; this anomaly became apparent during emptying of the primary circuit, before the vessel is opened. The facility's control team reacted immediately by interrupting the emptying operation and adding make-up water to the reactor vessel.This stage of emptying of the primary circuit, which is carried out while the core is loaded with fuel, is rather tricky as the water level must be reduced while still keeping a sufficient reserve above the core. | PWR | Operational | 1363 | 1988 | Level 2 on the French severity scale due to two independent failures during a single sequence. | 1 |  | 1 |  | T | 0 | 1
863 | 10 | 7 | 1991 | Léré, France | France | Energy | Plant | BELLEVILLE | 2 | 0 | 2 |  | WE | During a cold shutdown, after reloading of the core introduction in the primary circuit of ten cubic meters of pure water from a safety injection accumulator that had been hydro tested, the operators immediately added boron to the primary circuit. BASIS FOR RATING: Table A2 (addendum p. 9) with initiator possible. Within oprational limits and conditions: level 2. DIFFICULTIES IN RATING: Difficulties of classification of an event which is not foreseen in the design between the categories "expected", "possible", "unlikely". | PWR | Operational | 1363 | 1988 | Level 2 on French severity scale irreproducable | 1 |  | 1 |  | H | 0 | 0
864 | 20 | 8 | 1974 | Beznau, Switzerland | Switzerland | Energy | Plant | BEZNAU | 1 | 2 | 2 | 3 | WE | After a disturbance in the external electrical grid one of the two turbines shut down but a turbine bypass valve did not function; this caused the pressure in the steam generator to increase and subsequently the temperature and pressure in the primary system to rise. Both relief valves in the pressurizer opened but a few seconds later only one of them closed and the pressure in the primary system dropped leading to reactor scram and shut down of the second turbine. Water and steam poured out of the pressurizer through the stuck open relief valve and filled the drain tank. At 3 minutes the operator realized the situation and closed the block valve; a rupture seal on the drain tank blew, allowing primary water to spill onto the floor of the containment building. The high-pressure injection system was turned on and turned-off manually because conditions had stabilized. At 12 minutes procedures were initiated to bring the reactor to a cold shut down. | PWR | Operational | 380 | 1969 | TMI forerunner (operator here more conscientious). Serious incident | 1 |  | 1 |  | T | 1 | 20
865 | 8 | 2 | 2004 | Biblis, Germany | Germany | Energy | Plant | BIBLIS | B | 2 | 0 | 1 | WE | Both units (A and B) were in operation at full power when heavy storms knocked out power lines in the station vicinity. Because of an incorrectly set electrical switch and a faulty pressure gauge, the unit B turbine did not drop, as designed, from 1,300 to 60 megawatts, maintaining station power after separating from the grid, resulting in a reactor scram; all four emergency diesel generators started. Another emergency supply, over four trains from Biblis A, also started but, because of a switching failure, one of the lines failed to connect. These lines would have been relied upon as a backup to bring emergency diesel power from unit B to unit A, in case needed. The result was a partial disabling of the emergency power supply from Biblis-B to Biblis-A for about two hours. Then, the affected switch was manually set by operating personnel. | PWR | Permanent Shutdown | 1300 | 1976 | external event - partial degradation of back-up emergency system - interesting precursor | 1 |  | 3 |  | T | 1 | 10
866 |  | 6 | 1985 | Braud St. Louis, France | France | Energy | Plant | BLAYAIS | 4 | 1 |  | 1 | WE | Loss of residual heat removal; the operators allowed the water level to drop to an abnormally low level. Air was ingested into the RHR system and two pumps lost their prime. After 25 minutes, water had been resupplied and the pumps were restarted. The direct cause of the event was an erroneous assessment of the primary water level required to drain the steam generator tubes. The procedure was deficient. Also, the level must be decreased below the alarm setpoint, so there is no additional alarm available for the level at which pumps lose prime. The water level instruments were insufficient. Corrective actions include modifications in procedures and an improved level measurement system. | PWR | Operational | 951 | 1983 | “US NRC concluded, in a study on its Significant Determination Process, that the core damage frequency for a PWR whose level of protection was provided only strictly by legally enforceable requirements for mid-loop was on the order of 1E-2.” [cnra-r2006-4.pdf ] | 1 |  | 1 |  | H | 0 | 10
867 | 15 | 1 | 1991 | Jaslovske Bohunice, Czechoslovakia | Czechoslovakia | Energy | Plant | BOHUNICE | 2 | 2 | 2 | 1 | EE | During normal power operation a fire detector reported a fire in the room of the second category of reliability buses. The buses did not lose voltage. In order to repair damaged parts the operational personnel tripped the reactor by standard procedure. On 2% reactor power the bus was put off voltage and due to this two spray pumps became inoperable. Finally the reactor was brought in shutdown cooling mode. | PWR | Permanent Shutdown | 440 | 1980 | INES 2 justification missing | 0 |  | 2 |  | Fire | 0 | 10
868 | 21 | 11 | 1996 | Borssele, Netherlands | Netherlands | Energy | Plant | BORSSELE | Single | 2 | 2 |  | WE | Longer term operation of unit with insufficient containment function: It was discovered that a 15 cm diameter unfiltered containment venting line was actually open to the outside air, while its 4 block valves all registered "closed". It appeared that the valves had all been mispositioned, apparently as a result of maintenance work 9 months earlier. The deviation was corrected within 2 hours. | PWR | Operational | 515 | 1973 | INES 2 probably due to degradation of safety function | 1 |  | 1 |  | H | 0 | 0
869 | 15 | 6 | 1991 | Blackwater Estuary, United Kingdom | United Kingdom | Energy | Plant | BRADWELL | 1 | 1 | 2 |  | WE | During power raising the gas outlet temperature on one channel exceeded the Operating Rule limit for a short period. At the outset of this period the need for corrective action was recognized and bulk rods were inserted at an increased but insufficient rate to terminate the temperature transient. The rate of insertion did, however, ensure that the temperature rise was controlled. | GCR | Permanent Shutdown | 146 | 1962 | INES 2 due to inadequate safety function availability | 1 |  | 1 |  | H | 0 | 1
870 | 23 | 1 | 1990 | Tiverton, Canada | Canada | Energy | Plant | BRUCE | 4 | 2 | 2 |  | NA | During routine refuelling at full power, a reactor coolant leak of 1.4 t/hr developed in the fuelling vault. Operators determined that the east fuelling bridge had dropped 40 cm. The reactor was shutdown and cooled; coolant pressure was maintained by transfer from other units and recovery from sump. Total leakage was approx. 10% of the inventory. No safety system operation was required with the exception of containment box-up on high activity after one hour; no abnormal release of radioactivity to the environment. | PHWR | Operational | 830 | 1978 | INES 2 due to defence-in-depth degradation | 1 |  | 1 |  | T | 10 | 100
871 | 22 | 12 | 2012 | Tiverton, Canada | Canada | Energy | Plant | BRUCE | 1 | 2 |  | 1 | NA | The maintenance cooling system (MCS) pump tripped on electrical protection loss of one phase of off-site power. Operators attempted to restore maintenance cooling using the alternate MCS pump, but it failed to start. After several attempts, neither MCS pump could run for more than several minutes before tripping on electrical protection, and a loss of maintenance cooling was declared. At this point, the time to reach 90 C core temperature (cold shutdown limit) was more than seven hours. The direct cause of the loss of maintenance cooling was an ungrounded open phase condition on a 230-kV drop line to the in-service system service transformer. The high-voltage ground fault alarm, credited to monitor for open phase or imbalance conditions on the in-service TSS, did not alarm and indicate a fault. | PHWR | Operational | 830 | 1977 | limited safety significance/large safety margin - external, human | 1 |  | 3 |  | H | 0 | 1
872 | 21 | 8 | 1992 | Cattenom, France | France | Energy | Plant | CATTENOM | 1 | 2 | 2 |  | WE | During the annual shut-down for refuelling a filter has been discovered on a draining circuit of the reactor cavity. This filter, installed during the last outage period, should have been dismantled before the start up of the plant in 1991. The presence of this filter could affect the efficiency of the recirculation process in certain hypothetical situations. | PWR | Operational | 1362 | 1986 | Level 2 on the French severity scale as a potential impairment of a safety function | 1 |  | 1 |  | H | 1 | 10
873 | 12 | 6 | 1991 | Cattenom, France | France | Energy | Plant | CATTENOM | 4 | 1 | 2 |  | WE | On 12 June, when the reactor was undergoing startup tests and was operating for the first time at 30% of full power, a failure in the conventional part of the facility reduced the steam generator feedwater flow below the required minimum, and this triggered the automatic shutdown request. The order was in fact given, but the control rods did not drop into the core because of missing wiring in the two lines of the shutdown system. This incident had no safety consequences because the other protective actions taken brought the reactor into a safe state: the automatic shutdwon was not essential owing to the low power of the reactor, and the startup testing period thus had the advantage to detect the anomaly before the reactor was taken to higher power. | PWR | Operational | 1362 | 1991 | Level 2 of the French severity scale due to common mode failure of important safety system | 1 |  | 2 |  | T | 10 | 100
874 | 10 | 4 | 1991 | Pripyat, USSR_Ukraine | USSR_Ukraine | Energy | Plant | CHERNOBYL | 1 | 0 | 3 |  | EE | After unit shutdown for preventive maintenanc,e during the routine test of reactor overpower emergency protection in the low power range (LPEP) the failure of ionization chamber power supply cabinets of 3 trains out of 4 due to insulation damage of the +500 V power cable was found. The damage (melting) of cable insulation occurred due to high temperature in the room, where the cable route passes. Operating personnel activated only AZM protection (power level emergency protection) and started to perform refueling (unloading of the spent fuel assembly, installation of additional absorber) without activating the LPEP protection, which is forbidden by the procedure. In fact, because of the effect of Reactor Protection System (RPS) normal interlocking the LPEP protection could not be activated at any position of RPS control rods. | LWGR | Permanent Shutdown | 800 | 1977 | INES 3 due to operaton and safety culture deficiencies | 1 |  | 1 |  | T/H | 0 | 1
875 | 1 | 7 | 1991 | Pripyat, USSR_Ukraine | USSR_Ukraine | Energy | Plant | CHERNOBYL | 2 | n.a. | 2 |  | EE | While loading three new rejected fuel assemblies (FAs) into the shipping cask the rupture of the hoist cable with subsequent FA dropping occurred, which resulted in new FA damage. No damage to fuel rod cladding and no radioactivity releases occurred. The cause of cable rupture was the failure of the hoist end switch. BASIS FOR RATING: Initiator - real, possible (new FA dropping). Safety function availability - full. According to Table A2 level 1 (A-2R) is assigned. Event cause reveals safety culture deficiencies (deficiencies in organizational-technical measures for FA transportation) and therefore the level higher by 1 has been chosen. | LWGR | Permanent Shutdown | 1000 | 1978 | INES 2 (or 1) due to safety culture deficiencies | 0 |  | 2 (shipping cask) |  | T | 0 | 1
876 | 13 | 5 | 1996 | Avoine, France | France | Energy | Plant | CHINON | B1 | 0 | 2 |  | WE | During shut down for inspection and refuelling, the operator discovered while inspecting the civil engineering that the tie rods of the reactor pit lateral stops had loosened. The reactor pit is a concrete structure which supports the reactor vessel. It lies on the basemat and bears at the sides on the concrete which covers the basemat through 18 stops. Each stop is attached to the concrete with eight prestressed anchoring bars. This device is intended to absorb the horizontal stresses which could be generated during an earthquake, thus protecting the reactor vessel. Several of these bars were found to be loose and corroded, calling the reactor vessel pit's earthquake resistance into question. | PWR | Operational | 954 | 1982 | INES 2 due to equipment degradation questioning seismic resistance | ? |  | 3 |  | T | 1 | 50
877 | 19 | 9 | 1991 | Avoine, France | France | Energy | Plant | CHINON | B1 | ? | 2 |  | WE | A higher than foreseen boron concentration was dicovered on units B1 and B2, due to a calibration error on the measuring device. Common mode failure. | PWR | Operational | 954 | 1982 | Level 2 of the French severity scale due calibration error, violation of the technical specifications during the dilution process, lack of feed-back of experience (same incident at Dampierre in 1991), common cause failure | 0 |  | 1 |  | H | 0 | 0
878 |  | 7 | 1993 | Brownville, United States | United States | Energy | Plant | COOPER | Single |  |  |  | NA | Flooding. Dikes and levees collapsed around the site. An NRC Information Notice subsequently issued nearly a year later (NRC IN-94-27) indicated that below grade rooms in the reactor and turbine buildings had extensive leakage with rising water levels. The notice stated that “the floor drain system had backed up so that standing water from within areas known to be radiologically contaminated had migrated out into designated clean areas.” The NRC inspectors noted that plant personnel “had not established measures to divert the water away from important components.” For example, water levels rising inside the reactor building impinged on electrical cables and equipment such as the Reactor Core Isolation Cooling (RCIC) pump room causing the circuitry to ground out. “This event demonstrates that flooding problems and degradation of equipment may be caused by water inleakage even though flood waters are not above grade elevations,” the information notice indicated. The RCIC system is critical to plant safety in the event of loss of offsite power and a condition known as “Station Blackout.” | BWR | Operational | 801 | 1974 |  | ? | Natural hazards: external flood | 3 |  | H? | 1 | 10
880 | 27 | 6 | 2000 | Dampierre-en-Burly, France | France | Energy | Plant | DAMPIERRE | 1 | 1 | 2 |  | WE | When entering a shutdown state, the Safety Injection System was made unavailable due to the application of an erroneous operating rule, which does not permit to fulfill the requirements of technical specifications. This rule had been written by the Tricastin Plant and was also used as it was (i.e. with the error) by Dampierre and Bugey plants. | PWR | Operational | 937 | 1980 | INES 2 due to lack of safety culture/deficiencies in the quality insurance process | 1 |  | 1 |  | H | 0 | 0
881 | 14 | 12 | 1996 | Dampierre-en-Burly, France | France | Energy | Plant | DAMPIERRE | 1 | 2 | 2 |  | WE | A leakage has been detected on a piping connected to the primary circuit. The leak rate increased and led the operator to shutdown the reactor in order to localize the leak before reaching the safety threshold of 230 l/hour. The operator localized a non isolable primary water leak on a piping connecting the safety injection system to the plant primary system, probably due to thermal fatigue. The defected part of the pipe has been replaced during a one month outage. The damaged pipe length has been examined at the irradiated material workshop at Chinon and the preliminary expertise concluded to a through-wall crack located on a portion of straight piping and not on specific areas such as bends and welds as it could be expected. The most probable hypothesis is that the origin of this crack is due to a thermal fatigue due to a variation of temperature produced by cold water coming from non-tight valves located upstream. The operator, EDF, decided to make controls on straight parts of the piping during scheduled outages on 900 MW plants and, in some cases, decided specific outages. Other defects have been found on two pipes at Dampierre 3 in March 1997 and on Fessenheim 2 in April 1997 (so that other portions of pipes have been replaced and will be expertised). EDF has provided DSIN with a study on the evolution of the phenomenon. It appears that on a particular pipe small non-detectable defects can potentially lead to a through-wall crack within less of a cycle if these defects are initiated and stand small cold leaks from upstream valves. The analysis of this study by DSIN has led to re-rate the incident level 2. Still, EDF will give its strategy to solve this problem on the mean term by the end of June. Until the implementation of this strategy EDF will have to proceed to specific additional controls on these pipes. | PWR | Operational | 937 | 1980 | INES 2 probably due to degradation of safety function | 1 |  | 1 |  | T | 40 | 100
882 | 22 | 1 | 1992 | Dampierre-en-Burly, France | France | Energy | Plant | DAMPIERRE | 1 | 2 | 2 |  | WE | The operator discovered that the iodine filtering circuit of the control room ventilation system was unavailable. This anomaly was due to the presence (since 23 December 1991) of plugs in both the lines of the circuit. | PWR | Operational | 937 | 1980 | Level 2 on the French severity scale due to common mode failure of a system important for safety, in particular to inadequate procedure | ? |  | 1 |  | H | 0 | 0
883 | 25 | 11 | 1993 | Town of Newcastle, Canada | Canada | Energy | Plant | DARLINGTON | 4 | 2 |  | 1? | NA | A loss-of-flow event occurred, initiated by a switchyard transformer explosion, resulting in the loss of Class IV power to Unit 4 and a consequential turbine trip. The Reactor Regulating System responded by initiating a reactor stepback to 60 %FP. The HT pumps tripped because of the loss of Class IV power, significantly reducing the coolant flow through the channels. The resulting increase in heat transport system pressure was sufficient to activate opening of the LRVs, which provided pressure relief via discharge to the shell side of the bleed condenser. The bleed condenser high pressure alarm was activated shortly thereafter. As the HT pumps continued to run down, the measured flow in the SDS channels dropped below 20.5 kg/s, the HTLF setpoint for both SDS1 and SDS2 at reactor powers greater than 70% FP. A SDS1 trip was initiated at this time. Due to instrument sampling time, the SDS2 low flow trip was initiated shortly afterwards. | PHWR | Operational | 934 | 1993 |  | 1 |  | 2 |  | T | 1 | 20
884 | 5 | 10 | 2006 | Doel, Belgium | Belgium | Energy | Plant | DOEL | 1 | 0 | 2 |  | WE | The plant is equipped with 4 internal cooling fans to provide for cooling capacity inside the reactor containment after a Design Basis Accident and together with the spray system to reduce pressure and temperature inside the reactor containment. During the last outage period, the licensee performed additional verifications of the tightness of the containment cooling fans motors. These motors should be able to operate under severe environmental conditions (high pressure and temperature) and their tightness is required, according to the original qualification tests, to prevent significant introduction of water and/or steam into the motor casing. The leak tightness tests showed that all the motors were not in conformity with the test acceptance criteria, therefore the licensee could not demonstrate the availability of these motors under accident conditions. | PWR | Operational | 454 | 1974 |  | ? | containment cooling fans | 1 |  | ? | 0 | 10
885 | 1 | 9 | 1992 | Doel, Belgium | Belgium | Energy | Plant | DOEL | 3 | 2 (?) | 2 | 1 | WE | Recent results of the qualification testsof 3 electric containment penetrations as well as of other safety related connectors, for large loss of coolant and steam line break conditions, have shown that the insulation of the connectors is significantly degraded after a few minutes. While automatic protection of the reactor remains unaffected, the post accident control room activities could be made more difficult. After a detailed analysis of the situation it was concluded that the accidents can be mastered provided that additional procedural measures are taken. Some of the connectors have been modified immediately, others will be modified during the next refueling outage. | PWR | Operational | 1056 | 1982 | INES 2 not justified - probably due to degradation of containment safety functions and potential design flaws | 0 |  | 1 |  | T/H | 0 | 1
887 | 4 | 12 | 1990 | Dukovany, Czechoslovakia | Czechoslovakia | Energy | Plant | DUKOVANY | 1,2,3,4 | 2 for units 1, 2, 4; 0 for unit 3 | 2 |  | EE | A short circuit occurred in an external switching station and resulted in a disconnection of both 400 kV and 110 kV lines to all four units: Unit 1 failed to cope with the load rejection, it resulted in a reactor scram. Unit 2 and 4 reduced their power to the level of self-consumption. Unit 3 that had been shut down for refuelling, lost power supply and one of its two operable diesel generators (DGs) failed to start automatically. | PWR | Operational | 500 | 1985;1986;1986;1987 | INES 2 probably due to degradation of defence-in-depth with given initiator | 1 |  | 3 |  | T | 1 | 10
888 | 11 | 7 | 2003 | Romney Marsh, United Kingdom | United Kingdom | Energy | Plant | DUNGENESS | B1 | 2 | 2 |  | WE | Reactor 21 automatically tripped from full load on rate of change of Boiler Gas Outlet Temperature following a trip of the Main Boiler Feed Pump. The Emergency Boiler Feedpump was unavailable at the time of the trip due to maintenance. The Start-Up Boiler Feedpump was put into service manually when it did not automatically start, but it had to be shut down soon afterwards due to a priming oil pump problem which caused a small fire exinguished by the station fire team. With no high pressure feed pumps available the boilers were part depressurised using the Boiler Emergency Depressurisation Valves and the reactor cooled with feed provided from the Shut-Down Boiler Feedpump. Approximately one hour after the automatic reactor trip, the calculated average Gas Circulator Inlet Temperature for Boiler 22 exceeded the Operating Rule Limit of 300 degrees Celsius by 2.3 degrees for approximately 30-40 seconds. This was a consequence of starting the Gas Circulator Low Speed Pony Motors whilst the boilers were being fed by low capacity feed pumps. | GCR | Operational | 615 | 1983 |  | 1 |  | 1 |  | T | 1 | 10
889 | 19 | 11 | 1999 | Romney Marsh, United Kingdom | United Kingdom | Energy | Plant | DUNGENESS | B1,B2 | 0 | 2 |  | WE | While undertaking a boiler tube seal weld repair on a superheater on Reactor 21 a crack of significant extent was discovered in a weld adjacent to the tube plate. The mechanism for the crack was not yet determined and the potential could not be discountede for similar cracks to occur on Reactor 22 which would be outside the operational safety case. The conservative decision has been taken to affect a controlled shutdown of Reactor 22. Arising from the discovery a Project Team has been set up under the chairmanship of a company Engineering Division senior manager. The team will have responsibility for managing all aspects of the project including investigation of the causes, additional inspections, repairs and production of the safety case for return to service. Justification of Rating: Potential initiator with full safety function availability gives a basic rating upper limit of 2. The guidance then allows for adjustment dependent upon the likelihood that the defect would have led to component failure. The mechanism of component degradation is not yet fully understood, but the extent of the cracking is such that there appears to be little margin to failure remaining. Additionally, it is clear that the failure of this component was considered in the safety case to be unlikely, and therefore no routine surveillance programmes were in place to monitor the weld. Given the above situation, INES level 2 appears appropriate based on the current level of understanding. This is confirmed by verification as an incident with significant failures in safety provisions. | GCR | Operational | 615 | 1983;1985 | propose to downgrade to INES 1 | ? |  | 1 |  | T | 350 | 500
890 | 13 | 9 | 1991 | Fessenheim, France | France | Energy | Plant | FESSENHEIM | 1 | 2 (?) | 2 |  | WE | A metallurgical flaw (11 cm long, 3 cm deep) was discovered during checks carried out on one of the secondary circuit pipes feeding the turbine generator. BASIS FOR RATING: Potential consequences on the safety of the installation (third barrier fault). DIFFICULTIES IN RATING: This classification may be reassessed following the results of expertise. table A1 - inadequate – possible. | PWR | Operational | 920 | 1977 | difficult to rate (third barrier fault); reassessment envisaged | 0 |  | 2 |  | T | 0 | 1
891 |  |  | 1993 | Ohkuma-Machi, Japan | Japan | Energy | Plant | FUKUSHIMA-DAIICHI |  |  |  |  | A | There was an event at Fukushima Dai-ichi in 1993 where seawater from a corroded pipe leaked into the turbine building and flooded the emergency power supply. Based on this event (alone) a frequency of 10-3 per year for a scenario with a flooding of the below ground levels of the turbine hall and an extended SBO would have been merited. | BWR | Permanent Shutdown |  |  |  | 0 | Turbine buidling | 2 | corroded pipe | T | 0 | 1
892 | 4 | 9 | 1995 | Becancour, Canada | Canada | Energy | Plant | GENTILLY | 2 | 2 | 2 |  | NA | At 16:26 a heat transport (HT) leak due to a passing pressurizer drain valve was detected, allowoing hot D2O to flow directly into the HT collection system. The 0.5 kg/s leak filled the collection system with hot D2O and steam which backed up collection lines to other parts of the HT system, including the feed pumps. A total of 10m3 of D2O was spilled into several areas of the reactor building. A controlled shutdown of the unit was initiated at 18:20 with cooldown and depressurization achieved by 00:30 the next morning. A radiological alert was declared at 19:00 with increased airborne tritium concentrations in the reactor building . Following manual containment isolation reactor building pressure rose to 2.28 kPa. With the authorization of the advisory group the containment pressure was vented through driers. External release of tritium for the day following the event was estimated at less than 1% of the Derived Operational Limit. | PHWR | Permanent Shutdown | 675 | 1982 | INES 1 uprated to 2 because of common cause failure potential and procedural inadequacies | 1 |  | 1 |  | T | 1 | 10
893 | 4 | 3 | 1991 | Gravelines, France | France | Energy | Plant | GRAVELINES | 6 | 0 | 2 |  | WE | During the yearly outage for checking and refuelling an inspection revealed that 2 valves of an auxiliary circuit were blocked in close position. The investigations undertaken have shown that the valves have been blocked in closed position since the reactor began operating in 1985. As a result of this detection EDF has started a campaign for all other pressurized water reactors to verify the availability of valves of the same type which showed that 30 pressure valves were not operative. These were in circuits classed as "important for safety": in the component cooling circuit - and in the case of Gravelines - and in other circuits. Relating to other anomalies mentioned in Magnuc (information system of the French Nuclear Safety Authority, SCSIN) (anomalies of maintenance, of sand filters, anomalies in the installation of sump filters) which are affecting the quality of installation completion of pressurized water reactors, the Ministers of Industry and the Environment asked EDF to make a special effort to detect such problems. It is by making such an effort that EDF discovered that valves in certain auxiliary circuits were not in the right state to fulfill their function. It is therfore welcome to encourage the efforts made by EDF and to correct such anomalies; at first these efforts could lead to an increase in the anomalies detected. But on the other hand, it is appropriate to state that the final phase of reactor construction proves yet again that it may conceal some significant errors in the organization of quality control. Upgrading the level of quality control at certain construction sites appears even more indispensable. In the first analysis these anomalies found in the auxiliary systems classed as "important for safety" do not seem to have resulted in an important cummulative risk, but it is worrying that there has been lack of compliance with installation methods, with control and quality assurance of the circuits concerned, and this demands deeper analysis. | PWR | Operational | 951 | 1985 | Level 2 on the French severity scale due to degradation of safety-relevant systems of many plants | 1 |  | 1 |  | T | 0 | 10
894 | 23 | 2 | 1990 | Greifswald, Germany | Germany | Energy | Plant | GREIFSWALD | 4 (?) | 2 | 2 |  | WE | After checking the resin content of the K-filter and connection of the water cleaning system with the primary circuit, a leakage of the seal of the fill-in nozzle at the filter occurred. The nozzle is situated in the reactor hall out of the pressure room system. The personnel violated several operating instructions but the reactor was not shut down as prescribed in such situations. BASIS FOR RATING: No off-site impact, no on-site impact. Defence-in-depth (A-1R) 0/1. Violation of operating instructions, human error +1, with deficiency in safety culture = 2. DIFFICULTIES IN RATING: Judgement of the design deficiency by the containment aperture for the filter nozzle in the reactor hall and air ventilation system in the hall without filtration. | PWR | Permanent Shutdown | 440 |  | INES 2 due to violation of several operating instructions | 1 |  | 1 |  | H | 0 | 1
895 | 5 | 7 | 1990 | Greifswald, Germany | Germany | Energy | Plant | GREIFSWALD | 5 | 0 | 2 |  | WE | After the monthly control of the nuclear monitoring system it was not noticed by the personnel, that the ionization chambers of the low and middle range of that system after controlling were driven out of their working range and not driven back. This faulty position was observed 24 hours later after controlling by a shift-physicist. During this period the nuclear monitoring system for the cold shutdown stage of the reactor was not available. The shutdown concentration of boric acid in the primary circuit during this time was 17.1 g/l. | PWR | Permanent Shutdown | 440 | 1989 | INES 2 probably due to degradation of defence-in-depth | 1 |  | 1 |  | H | 0 | 0
896 | 27 | 2 | 2016 | Yeonggwang-gun, South Korea | South Korea | Energy | Plant | HANBIT | 1 | 2 | 1 |  | A | Turbine trip/Reactor trip due to loss of condenser vacuum. During normal operation, loss of condenser vacuum caused reactor trip. During transient period, turbine driven auxilary feed water pump as tripped. Event sequence was,1) Condenser A Expansion joint seal water low-level alarm occured, 2) condenser A expansion joint breach confirmed, 3) although emergency recovery action was taken, failed to recover condenser vacuum, 4) main turbine tripped and thus reactor tripped. Cause of breach of condenser expasion joint was aging. | PWR | Operational | 1032 | 1986 | Mechanical failure | ? |  | 2 |  | T | 50 | 90
897 | 28 | 2 | 2014 | Yeonggwang-gun, South Korea | South Korea | Energy | Plant | HANBIT | 2 | 2 | 1 |  | A | During normal operation, a CEA (control element assembly) dropped by the inadequate opening of a motor-generator set output breaker in the process of the 1st periodic test of the Automatic Seismic Trip System (ASTS). The reactor was tripped but the turbine was not tripped because there was no turbine trip signal unlike reactor protection signal. The sustained turbine operation caused the rapid decrease of the main steam line pressure, and the Safety Injection System was actuated by main steam line low-pressure. Upon investigation, it was identified that there was an error in an electric contact of ASTS circuit; it was also identified that there were insufficiencies in the alarm system and management of design change and test. | PWR | Operational | 1028 | 1986 |  | ? |  | 2 |  | T | 10 | 20
898 | 1 | 10 | 2014 | Yeonggwang-gun, South Korea | South Korea | Energy | Plant | HANBIT | 2 | 0 | 1 |  | A | During an overhaul, a switchyard circuit breaker was opened by protective relay actuation of Start-Up Transformer (SUT) on a test after the replacement of a high voltage circuit breaker of 13.8kV non-safety bus. The off-site power was lost and emergency diesel generators started automatically due to low voltage at the 4.16kV safety bus. Upon investigation, the licensee’s pre-review about the probability of protective relay actuation in the condition of energized SUT was inadequate. | PWR | Operational | 1028 | 1986 |  | ? |  | 1 |  | H | 0 | 0
899 | 23 | 3 | 1999 | Yeonggwang-gun, South Korea | South Korea | Energy | Plant | HANBIT | 2 | 1 | 1 |  | A | The reactor was starting up after the shutdown due to the failure of main generator on March 23, when actuation of condenser steam dump valves caused the feedwater control system transient while dumping the surplus steam, which was generated in the steam generator, to condenser. Subsequently, while controlling the S/G water level, the TBN and reactor were tripped due to the S/G water level high-high signal. The failure of the condenser steam dump valves was due to failed actuation of the condenser steam dump valve (one of three valves in the condenser dump valve group #1). It increased the power deviation between the reactor and the TBN, and opened the 6 valves in the dump valve group #2. Therefore, too much steam was released to condenser, and S/G pressure was relieved. The S/G water level rapidly increased due to the swelling, and it caused TBN trip and actuated feedwater isolation signal. In spite of the activities to supply main feedwater and to recover the water level, the opening of the main feedwater isolation valve was delayed, and subsequently, the reactor tripped owing to S/G water level low-low signal. All the safety parameters were maintained within the allowable range, and there was no impact on the reactor safety. Besides the failed actuation of pressure balancing valve of the condenser dump valve, it was found to be hard for the operator to predict the plant status correctly and understand the characteristics and functions sufficiently. In other words, the operator could not properly cope with the failed actuation of the dump valve even though recognizing it in advance, and operated the unit without incorporating operating experience that TBN startup should be commenced at above 15% reactor power. Condenser steam dump valve was dismantled and inspected, and startup operating procedure was revised to prevent transient at low power. In addition, SGWLCS (Steam Generator Water Level Control System) was changed to a digitally-controlled SGWLCS. The reactor reached to the criticality at 02:38 on March 24 and synchronized at 05:14 on March 25. While evaluating INES (International Nuclear Event Scale) grade, it was upgraded by applying “safety culture deficiencies” as the operator did not observe the procedure, and thus evaluated as “Scale 1.” | PWR | Operational | 1028 | 1986 |  | ? |  | 2 |  | T;H | 0 | 1
901 | 20 | 12 | 2016 | Ulchin-gun, South Korea | South Korea | Energy | Plant | HANUL | 5 | 2 | 1 |  | A | Manual reactor trip for maintenance of heated junction thermocouple instrumentation flange assembly of reactor vessel. | PWR | Operational | 1051 | 2003 | Mechanical failure | ? |  | 1 |  | T | 80 | 120
902 | 17 | 1 | 2013 | Ulchin-gun, South Korea | South Korea | Energy | Plant | HANUL | 1 | 2 | 1 |  | A | During normal power operation, a power range high flux rate protection signal was generated from ex-core nuclear instrumentation, and reactor was tripped. Upon investigation, while at work to correct the abnormal condition of the ‘power range high flux rate’ trip signal at channel 2 replacing the malfunctioned channel, the additional signal was activated from channel 3 due to the abnormal signal of the channel. As a result, reactor was tripped by the coincident logic signals at the both channels (2/4 logic circuit). Causes and Corrective Actions It was identified that the malfunction was due to an improper polarity installation of the tantal capacitor in upper-lower channel power summation card in accordance with the erroneous design drawing. The following corrective actions were implemented. - Replacement and test of the power summation card with correct polarity installation of the tantal capacitor - Inspection on circumjacent equipments and validation of their integrity - Planning of the detailed inspection on the cards by manufacturer | PWR | Operational | 1008 | 1988 | Instrumentation error | ? |  | 1 |  | T | 10 | 20
903 | 26 | 11 | 2012 | Ulchin-gun, South Korea | South Korea | Energy | Plant | HANUL | 6 | 0 | 1 |  | A | During refueling outage, inadvertent Safety Injection (SI) occurred due to reactor protection signal in the process of Reactor Coolant System (RCS) heat up for the plant startup. Upon investigation, it was identified that pressurizer low pressure setpoint was set improperly due to the missing out of system restoration after the calibration of plant protection system and the omission of set point check steps (initial condition and notice) in General Operating Procedure (GOP) for RCS startup. And reactor protection signal (pressurizer low pressure signal) occurred at pressure 35kg/m2 in the RCS heat up process. Causes and Corrective Actions This event occurred due to pressurizer low-pressure false signal caused by accumulated human errors. The following corrective actions were implemented. | PWR | Operational | 1051 | 2005 |  | ? |  | 1 |  | H | 16 | 20
904 | 7 | 5 | 2006 | Ulchin-gun, South Korea | South Korea | Energy | Plant | HANUL | 1 | 1 | 1 |  | A | During Reactor Coolant System(RCS) heatup following the completion of overhaul maintenance, the Ulchin Unit 1 experienced a spurious Safety Injection(SI) due to the “Main Steam Line High Differential Pressure” at 21:44 on May 7, 2006. Upon investigation, it was verified that the main steam line pressure of the Steam Generator(S/G) ‘B’ continuously indicated zero bar(g) even though those of S/G ‘A’ and ‘C’ were increasing when the unit experienced the Main Steam Line High Differential Pressure. Because the isolation valve of the main steam line B pressure transducer was closed, the main steam line pressure of S/G ‘B’ was not being measured. The I&C contractor personnel who carried out the calibration for the S/G pressure transducer on April 18 did not reopen that isolation valve after the calibration, and so the isolation valve of the main steam line B pressure transducer was inadvertently closed. Following the actuation of SI, all the safety-related systems and components were operated as expected and the emergency operating procedure for the spurious safety injection was entered and exited about 5 minutes after the SI actuation. Since the RCS pressure was above the shutoff head of the LHSI(low head safety injection) pump, SI flow into the RCS did not occur. The plant was maintained in operational mode 5 after SI termination so that the RCS pressure could be controlled via the pressurizer. | PWR | Operational | 1008 | 1988 |  | ? |  | 1 |  | H | 5 | 6
905 | 11 | 10 | 2006 | Ulchin-gun, South Korea | South Korea | Energy | Plant | HANUL | 2 | 1 | 1 |  | A | During plant startup following the completion of unscheduled maintenance work for the main generator hydrogen leakage with the reactor at critical condition on Oct. 11, 2006, the RCS pressure was identified to be decreased abnormally. The operator discovered that the pressure decrease was due to fail-opening of the pressurizer spray valve and took immediate actions to recover the RCS pressure. The following are the plant responses and the operator actions in time sequence. 13:30 Complete the maintenance work for the hydrogen leakage of main generator. 14:05 Start heat-up operation for the main steam-line 14:40 Reactor critical 15:37 Identify RCS pressure decrease and discover fail-opening spray valve(RCP 001VP) 15:40 Stop RCP #003PO to isolate the spray flow Enter into subcriticality using control bank insertion 15:41 Intentional blockage of SI signal upon P-11(at 134bar.a) 15:47 RCS pressure reached the pressurizer low pressure SI setpoint(118.7bar.g) 15:49 Stop RCP #002PO 15:54 Start RCP #002PO and stop RCP #001PO 15:55 RCS pressure reached 111bar 16:00 Inspect spray valve(RCP 001VP) 16:20 Manually close spray valve(RCP 001VP) in the field 16:22 Start RCP #001PO 16:26 RCS restored NOP(155bar) and NOT(286℃) With an abnormal depressurization condition, the operator intentionally blocked the SI signal which ought to be done during normal cooldown operation only. Even with RCP #003PO and #002PO stop the RCS depressurization continued. During further depressurization, the operator should have actuated the manual SI when the pressure decreased to the low pressre SI setpoint(118.7bar.g) but the shift crew could not actuate manual SI. And they only considered the fail-opening of spray valve and neglect any other possible accidental condition in the FSAR. This was an evident and intentional inappropriate defeat of safety injection. When the operator stopped RCP #001PO, the primary system recovered normal pressure and temperature. After recovering the RCS pressure the plant was maintained in hot standby condition and the RCS pressure was maintained at 155 bar. Upon investigation, one of the two spray valves was found to be fail-open due to loosening of the travel pin nut which comprised the pneumatic positioner of the spray valve. Thus the travel pin was separated from the assembly which resulted in the actuation of the rotary shaft arm and continuous supply of IA(instrument air) to the valve and this caused the valve to fail-open. During the previous 13th overhaul, the valve positioner was replaced with a new one and the travel pin and nut was reassembled. It was estimated that there were some inferiorities while carrying out the reassembling work. There was an unmeasurable and unaccountable loss of safety function associated with this inappropriate defeat of SI and there were a great deficit in the safety culture of the shift operators and the utility. But there was no radiation release to the site nor to the environment. | PWR | Operational | 1012 | 1989 | Instrumentation error | ? |  | 1 |  | T | 6 | 8
906 | 5 | 4 | 2002 | Ulchin-gun, South Korea | South Korea | Energy | Plant | HANUL | 4 | 0 | 1 |  | A | Ulchin Unit-4 was shutdown on April 5, 2002, for 3rd refueling outage. At the beginning stage of plant cooldown, at 18:33, the operators observed notable decreasing of pressurizer level and pressure and, in response, the operator isolated the CVCS letdown with starting of the third charging pump to compensate the loss of primary coolant inventory. During the operator counter actions, at 18:46, the radiation monitors of SG #2 sampling line alarmed with the increasing of SG #2 level to diagnose the operators the event as SGTR. The operators isolated the affected SG and actuated the safety injection (SI) according to the EOP. The pressurizer level was recovered by the HPSI flow, and the reactor was depressurized and cooled down using the intact SG to terminate the leak flow. At 19:59, the RCS and SG pressures were equalized, and the SI was terminated followed by plant cooling down using SG backfill operation. At 02:58 on the following day, the plant went into the shutdown cooling system operation and exit from EOP. At 13:25, the plant reached cold shutdown condition. No environmental impact and no radiation exposure of the plant staff were reported. After the event, the close investigation was performed and the result showed that single tube located at hot-leg side of SG #2 was ruptured circumferentially due to primarily on the PWSCC. As the results, tube plugging for affected tubes and installation of stabilizer for adjacent tubes of SG #2 were conducted. In addition, the post actions including the reinforcement of SG maintenance program were accompanied. The rating of the event was determined as level 1 based on the point of the defence in depth criteria of INES manual. | PWR | Operational | 1053 | 1998 |  | ? |  | 1 |  | T | 1 | 10
907 | 11 | 12 | 1998 | Ulchin-gun, South Korea | South Korea | Energy | Plant | HANUL | 1 | 1 | 1 |  | A | While cutting back the power, a leakage occurred due to the damage on the pipes of the NSCW (Nuclear Service Cooling Water) system. But, the operator failed to recover it and this train became inoperable status. So, according to the technical specification, the operator manually shut down the reactor. After the shutdown, the operator switched it over to operation mode ‘5’ and removed the residual heat through RHRS (Residual Heat Removal System) and S/G. The damage of the NSCW system pipes was appeared to be due to the disconnection of some steel wires caused by the long-term corrosion of the internal cylinder and steel wires, as the pipes were established inside of the concrete gallery that can be easily corroded. The licensee covered the NSCW system with temporary plate for prompt recovery, and replaced the pipes damaged during an overhaul and the neighboring pipes that cracking was detected. Also, in the long term, the licensee determined to strengthen the investigation on the NSCW system pipes and the concrete gallery and to perform minute investigation on the cracking or leakage of the NSCW system pipes every 5 years. | PWR | Operational | 1008 | 1988 |  | ? |  | 1 |  | T | 90 | 130
908 | 17 | 1 | 1997 | Ulchin-gun, South Korea | South Korea | Energy | Plant | HANUL | 2 | 2 | 1 |  | A | While performing an emergency trip logic test after high neutron flux low setpoint trip test at around 11:37 during normal operation, as not recognizing the situation that the reactor trip breaker was opened by the malfunction of Block Relay, the reactor trip bypass breaker was opened at 13:01 and it caused the reactor to trip. Usually, trip signal should be blocked when removing inhibition signal after a low setpoint trip test. However, as the trip signal was not blocked due to bad contact, the reactor trip breaker was opened as the inhibition signal was removed. Although the reactor trip breaker was opened at around 11:37, the operator neglected it for about 1 hour and 20 minutes, and overlooked the failed status of trip breaker status light. Also, he did not check the position of the trip breaker. In addition to it, it was confirmed that the management of related regular/periodical test was inappropriate and the inspection on relays were insufficient. To prevent recurrence, the licensee strengthened the inspection procedure on the block relay and complemented the test procedure. Also, he prepared a reactor trip breaker operation procedure and improved the operation procedures for principle components. | PWR | Operational | 1012 | 1989 |  | ? |  | 1 |  | H | 0 | 0
909 | 18 | 9 | 1990 | Visaginas, Lithuania | Lithuania | Energy | Plant | IGNALINA | 1 | 2 | 2 |  | EE | Effort was in progress to repair the faulty pressure gauge of the main safety valve (MSV) of the primary circuit. In the course of this activity 2 MSVs out of 12 opened, and the steam was received by the accident isolation system as designed. Partial steam release to environment occurred through the clean air venting facility of the isolation system decay chamber without exceeding permissible limits. Once personnel activated the lines of forced closure, the above two valves closed. Repair of the faulty pressure gauge was performed - without the established work program, combined with the failure to take technical measures aimed at preventing unauthorized opening of MSVs. | LWGR | Permanent Shutdown | 1300 | 1983 | INES 2 probably due to degradation of defence-in-depth and deficiencies in operational procedures (during maintenance) | 1 |  | 1 |  | H | 0 | 0
910 | 4 | 10 | 1990 | Visaginas, Lithuania | Lithuania | Energy | Plant | IGNALINA | 1 | 2 | 2 |  | EE | While connecting diesel generator (DG)-5 to essential bus during routine test the bus section was deenergized. This caused the stop of turbo-generator (TG)-2 lub-oil system pump fed by this bus. Due to defect in the standby feature activation system the standby oil pump failed to start. A signal of oil tank level and oil pump discharge pressure decrease was formed and TG-2 was tripped by protection system. Reactor power was reduced to 50% by TG trip protection. The cause of bus failure was wrong connection of DG-5 power cable to the bus after maintenance. BASIS FOR RATING: Initiator - essential bus deenergization. Event expected, real. Safety function availability within safe operation limits and conditions, which corresponds to level 1/2 (B-1R). The event showed personnel errors, that demonstrate poor "safety culture", therefore the maximum level has been chosen. | LWGR | Permanent Shutdown | 1300 | 1983 | INES 2 probably due to degradation of defence-in-depth and deficiencies in operational procedures (during maintenance). Interesting sequence. | 1 |  | 1 |  | H (during maintenance) | 0 | 10
912 | 15 | 8 | 1976 | Karachi, Pakistan | Pakistan | Energy | Plant | KANUPP | 1 | 1 |  | 2 | A | Plant was warming up when surge tank (pressurizer) heater vessel level dropped below the heaters while surge tank was pressurized. Heaters kept operating and surge tank heater vessel outlet pipe fractured due to high temperature at normal operating pressure resulting in a small LOCA. No fuel damage. | PHWR | Operational | 100 | 1971 |  | 1 |  | 1 |  | T | 0 | 1
913 | 26 | 2 | 1991 | Netishyn, USSR_Ukraine | USSR_Ukraine | Energy | Plant | KHMELNITSKI | 1 | 2 | 3 |  | EE | On 26.02.91 at 03.47 routine operability test of safety system train 1 was in progress. Operating personnel has identified the failure to control the valve at the discharge side of the High Pressure System (HPSI) pump due to a disconnected power cable of the above valve. The deficiency was eleminated and valve operability check was performed. One day later at 11.40 inoperability of all three HPSI system trains were eliminated without reducing the unit power. Disconnection of power cables from HPSI pump valve motors was performed on 04.02.91 after unit shutdown in the course of cooldown process to avoid reactor vessel water hammer effect in cold condition at possible unauthorized start of these pumps. However, due to deficiencies in the work and surveillance program and in the design as regards valve position monitoring from the control room, the power supply was incompletely restored and this ocurrence was not discovered during the prestart testing. Breach of unit safe operation condition occurred as regards the number of operable HPSI system trains. | PWR | Operational | 1000 | 1987 | INES 3 due to degradation of defence in depth, failure over long time and lack of safety culture | 1 |  | 1 |  | H | 0 | 0
914 | 3 | 3 | 1994 | Polyarnye Zori, Russia | Russia | Energy | Plant | KOLA | 2 | 1 | 2 | 1 | EE | The unit was in maintenance. At 19:35, while performing the reactor cooldown effort, a coolant leak from a NB50 pipeline of the primary water makeup system into the sealed rooms occurred. At 21:03 the leak was stopped by isolating the affected pipeline. The leak from the pipeline was isolated under the normal design configuration. Radiation situation in the attended rooms, on-site and off-site remained unchanged. Activity releases through the vent stack above limits prescribed for normal operation did not occur. | PWR | Operational | 440 | 1974 | This event is rated under the "degradation of defence-in-depth" criterion. Real initiator occurred - "small loss of coolant accident" (initiator frequency - medium/possible). Safety function availability - full. For this initiator the basic rating according to Table II (A2) of the INES User's Manual (1992 revision) is 1. The event revealed additional factor that required uprating - Safety Culture deficiencies: violation of the operating procedure (exceeding of permissible difference of coolant temperature in pressurizer and in reactor core outlet); operator switched off the emergency makeup pumps without justification; deficiency of procedure on detection of the primary leaks. | 1 |  | 1 |  | T | 0 | 1
915 | 2 | 2 | 1993 | Polyarnye Zori, Russia | Russia | Energy | Plant | KOLA | 1,2 | 2 | 3 |  | EE | As a result of a tornado the 330, 154 and 110 kV transmission lines were damaged. At 02:27 and 02:32 turbogenerator 1 and 2 were tripped by system emergency protection as a result of strong frequency oscillations in the system. At 02:32 reactor shutdown upon AZ-1 signal, actuated on core pressure difference increase above setpoint because of increased flowrate of the Reactor Coolant Pumps as a result of grid frequency rise up to. The normal Diesel Generators (DGs) 1,2 and the standby diesel (SD) started for coast down as designed. Since the auxiliary power buses were under voltage, DGs 1,2 tripped after 1.5 mins of operation according to design algorithm. Personnel transferred DGs 1,2 and SD to manual control and auxiliary power was supplied from service transformers. Main steam header pressure maintaining and residual heat removal were performed using turbine bypass check valves (venting steam to condensers) and steam dump valves (controlled bleed to station service collector). Steam generator (SG) levels were nominal. Preparations were started to bring the reactor to the minimum controlled power level. At 03:33 AZ-1 signal was formed again. DGs 1,2 and SD failed to start due to their unavailability for the start-up (they were on manual control). Significant voltage oscillatios at 6 kV auxiliary buses subsequently followed. By 04:00 the primary cause of the AZ-1 scram signal was eliminated; DGs 1,2 and SD were brought to automatic control. At 04:11 at voltage decrease AZ-1 signal was formed on Reactor Protection System (RPS) feeders deenergization. DGs 1,2 and SD started. DGs 1,2 failed to get connected to essential buses since the latter were under voltage and after 1.5 mins of operating tripped. Since the AZ-1 signal for DGs start persisted, DGs 1,2 periodic restarts followed which led to exhausting the air inventory in the DGs startup air bottles. Core cooling was maintained through natural circulation. The SD remained in service at coast down but at 04:26 was tripped by the oil pressure protection. Subsequent attempts to supply power to auxiliary buses from the DGs were unsuccessful due to absence of air in the startup bottles. At 06:15 as a result of system accident progression total loss of power occurred. DGs 1,2 and SD failed to start due to insufficient air pressure in the DG startup air bottles. The vital buses were connected via the reversible motor generators to the batteries. Core cooldown was performed via SGs in the natural circulation mode with steam dumping. At 06:45 unit power supply from the off-site source was restored. Throughout the transient core status was being monitored with the help of design-provided (normal) instrumentation. | PWR | Operational | 440 | 1973;1974 | INES 3 due to violation of unit safe operation limits and conditions, DGs and SD unavailability to perform safety function plus lack of safety culture. Very interesting precursor/ LOOP forerunner | 1 |  | 3 |  | H | 1 | 10
916 | 17 | 11 | 1992 | Polyarnye Zori, Russia | Russia | Energy | Plant | KOLA | 1 | 1 | 2 |  | EE | The unit was at 3% of thermal nominal power with turbogenerator (TG)-2 at coast down and TG-1 under maintenance. A short circuit occurred in the armature winding of the reversible motor generator (RMG-1) connected to the unit DC panel (UDCP-1). Automatic breaker which disconnects UDCP-1 from RMG-1 failed to open. The resulting current oscillations have led to the opening of the automatic breaker which supplies power to Reactor Protection System (RPS) emergency protections panels from UDCP-1. The automatic breaker of the same panels fed from the common unit DC panel opened on unexplained cause. Because of loss of voltage on the RPS panel AZ-1 protection actuated and the reactor was scrammed. The signal for diesel generators (DG) start was generated. The prestart oil circulation pumps (POCP) of these diesels fed from UDCP-1 started. Because of the total short circuit current in RMG-1 generator and the load current including the POCP starting currents, the automatic breaker connecting UDCP-1 to the battery opened. The automatic breaker feeding UDCP from RMG-1 was opened manually. As a result of UDCP deenergization operating DC supply to control circuits of some mechanisms without standby sypply from other DC panels was lost. This resulted in the failure to start two service DGs and one standby DG, loss of remote control function of safety injection pumps, emergency feedwater pumps, SG safety valve and normal operation systems mechanisms. 20 mins later the power to UDCP-1 was supplied through the mutual redundancy grid from the common unit DC panel. Reactor parameters remained under control and within safe operation limits. No on-site or off-site impacts. | PWR | Operational | 440 | 1973 | INES 2 due to degradation of defence in depth. Interesting event sequence - precursor study candidate | 0 |  | 2 |  | T | 0 | 1
917 | 16 | 5 | 1991 | Polyarnye Zori, USSR_Russia | USSR_Russia | Energy | Plant | KOLA | 3 | 2 | 2 |  | EE | During the routine test of the 3QW (?) diesel generator (DG), the failure of its control system occurred. The DG was taken out of service for maintenance. 5 hours 41 minutes after the event the affected DG was tested under load and placed in expectation mode. While taking the affected DG out of service for repair personnel failed to test the two remaining safety system (SS) trains, which constitutes a breach of technological procedure requirements. BASIS FOR RATING: Initial event -failure of one SS train. Event - expected, postulated. Safety function availability - sufficient, which correponds to level 1/2 (C-1P). The event reveals safety culture deficiencies (item 4.2 b), therefore level 2 has been chosen. | PWR | Operational | 440 | 1981 | INES 2 due to lack of safety culture | 1 |  | 1 |  | H | 0 | 1
918 | 3 | 9 | 2015 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 4 | 2 | 1 |  | A | During normal operation, the reactor was tripped by reactor protection signal (RCS flow low). Upon investigation, it was identified that 1) ground fault occurred at the surge protector of RCP (reactor coolant pump) ‘B’, 2) main breaker and back-up breaker were tripped by actuation of the ground relay, 3) the RCP was tripped, 4) the RCS flow low signal was generated, 5) the reactor was tripped. | PWR | Operational | 1044 | 1985 |  | ? |  | 1 |  | T | 19 | 25
919 | 14 | 4 | 2013 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 4 | 1 | 1 |  | A | During reactor coolant system (RCS) depressurization and cooldown after reactor manual shutdown, safety injection (SI) occurred by main steam line low pressure signal at S/G ‘C’. Upon investigation, during the RCS depressurization and cooldown, main steam was over-released to condenser by main control room operator and main steam line pressure decreased quickly due to excessive cooldown of RCS. After stop of steam release to condenser, RCS cooldown and main steam line pressure decrease was still continued through S/G blowdown. But, because of insufficient monitoring of operating parameter, main steam line pressure decreased to low pressure set-point and SI occurred. 23.7 tons of coolant was injected to RCS by SI, but it was verified that the fast cooling effect was negligible in terms of the thermal stress and fatigue. In the process of SI, pressurizer relief tank (PRT) rupture disk burst and 2.3 tons of coolant was spilled over to the reactor containment sump. Causes and Corrective Actions The event was caused by operator’s error not observing cooldown procedure. The following corrective actions were implemented. - Replacement of PRT rupture disc | PWR | Operational | 1044 | 1985 |  | ? |  | 1 |  | H | 0 | 1
920 | 14 | 4 | 2013 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 4 | 1 | 1 |  | A | During power ascension after recriticality, licensee shutdown reactor manually for inspection on foreign material alarm of loose part monitoring system in feedwater-side of S/G ‘A’. Upon investigation, a circle object (diameter: 40mm, height: 21mm, weight: 152.4g) was found in annular space of S/G hot leg. It was verified that the object was magnetic fixing material which was used to fix lighting during the replacement of S/G moisture separator in 2011 overhaul and it was not removed after the work. Causes and Corrective Actions The following corrective actions were implemented. - Inspection on S/G ‘A’ tube with eddy current examination - Foreign material inclusion inspection in all S/Gs (A, B, C) - Designation of chief manager at important area and management reinforcement of take-in and out item lists for foreign material inclusion prevention | PWR | Operational | 1044 | 1985 |  | ? |  | 2 |  | H | 30 | 50
921 | 19 | 4 | 2011 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 3 | 0 | 1 |  | A | The bus protection relay was actuated by human error while survey on 13.8kV bus in the turbine building during overhaul in Kori Unit-3. At the time of survey, one of two off-site power bus was energized for surveillance of switch yard PCB. Low voltage signal on the safety buses in Kori Unit-3 and 4 due to the loss of off-site power on the 4.16kV safety bus caused by ground fault which occurred due to the confusion of maintenance personnel for the equipment. As a result, the emergency diesel generators started up and supplied power on the safety buses except EDG A in Kori Unit 4 that started manually 6 min. later due to the failure of control power. During the transient of power grid, Kori Unit-3, Unit-4 under overhaul and power operation had some effects such as pump stop and start, Two Units were maintained stable condition and normal power operation. | PWR | Operational | 1044 | 1985 | Causes and Corrective Actions licensee had performed a detailed causes analysis, test and maintenance for affected parts, and surveillance test for the delayed power supply on the EDG-A in Kori Unit-4. The following corrective actions were implemented. - Enforcement work control for preventing of human errors - Restriction work of low voltage on the safety bus during overhaul period - Reinforcement on management and education of subcontractor - Establishment a long-term plan for advanced off-site power supply system Safety Assessment While the system transient state was caused by mistake of maintenance personnel, the emergency diesel generator started up due to the loss of voltage properly. There was no problem with the nuclear safety. There was no adverse effect on the plant safety or radioactive material release to the environment as a result of this event | ? |  | 2 |  | H | 0 | 0
922 | 21 | 6 | 2011 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 2 | 2 | 1 |  | A | Experienced a reactor trip due to the Reactor Coolant Pump trip. Upon the investigation, it was identified that the RCPs tripped due to the actuation of the differential protective relay caused by the ground fault on the 345kV power grid between Shin-Ulsan and Kori Unit-2 swichyard. According to the results of survey on the faulted power grid, An foreign material(vinyl for vinyl house) was found which initiated power transients on the grid. Also investigation team evaluated some setpoint errors caused by miscalculation of actuation setpoint for reverse power relay of the generator circuit breaker which designed to open breaker during power transfer from on-site power to off-site power. Causes and Corrective Actions licensee had performed a detailed causes analysis, test and maintenance for affected parts The following corrective actions were implemented. - Evaluated setpoint of the reverse power relay for generator protection - Performed functional test for reverse power relay - Reinforcement on design change and setpoint control - Enforcement of operational experience system Safety Assessment There was no problem with the nuclear safety. There was no adverse effect on the plant safety or radioactive material release to the environment as a result of this event | PWR | Operational | 681 | 1983 |  | ? |  | 3 |  | T | 8 | 12
923 | 17 | 11 | 2000 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 1 | 1 | 1 |  | A | the plant was increasing power after periodic refueling outage. The reactor reached critical at 00:15 on November 17. At the reactor power of 2%, the operator was trying to test turbine driven auxiliary feedwater pump. The operator should have manually operated the flow control valve that supplies steam to the pump for the test but he pushed on steam generator level low-low signal button instead to open the flow control valve without blocking the reactor trip. Temporary investigation showed the operator didn't realize the reactor already reached critical. The reactor tripped at 20:43 on the same day. The plant is returning to normal operation and there was no impact on reactor safety. | PWR | Permanent Shutdown | 607 | 1977 |  | ? |  | 1 |  | H | 0 | 0
924 |  | 6 | 1984 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 2 | 0 |  | 1 | A | There was a loss of reactor heat removal (RHR) while at midloop during refuelling. Due to an instrument error, there was a false low-low level signal generated from the reactor water storage tank (RWST), and, as a consequence, the signal transferred the suction supply to the containment sump (which, of course, was dry at this time). The operating RHR pump failed due to loss of suction supply. The primary system increased in temperature by 95 C, there was steaming from the primary system; a number of actionswere taken by the operating staff; RHR was off for about one hour. | PWR | Operational | 681 | 1983 | minor safety significance - human (procedural), technical | 1 |  | 1 |  | H;T | 0 | 1
925 |  | 10 | 1987 | Gijang-Gun, South Korea | South Korea | Energy | Plant | KORI | 3 | 0 |  | 1 | A | Loss of suction to the pumps of the heat removal system (RHR) during the reactor cooling system (RCS) draining operation. The RHR was off for about 40 minutes, until level was restored by draining from the storage tank (RWST). Primary temperatures rose to almost the boiling point. | PWR | Operational | 1044 | 1985 | minor safety significance - human (procedural), technical | 1 |  | 1 |  | H;T | 0 | 10
927 | 19 | 5 | 1998 | Vratza, Bulgaria | Bulgaria | Energy | Plant | KOZLODUY | 1 | 0 | 2 |  | EE | During refuelling outage, the fuel loading of the reactor was completed and the concentration of H3BO3 in the primary circuit was 12g/l. During the decontamination of secondary side of steam generator 3 by chemical solution a rupture of the blow-down pipe occurred and part of the solution was spilled in the steam generator compartment. The solution then reached the emergency boron tank and polluted it with chemical products. On 20-21 May the tank was drained, cleaned and filled again with concentration of H3BO3 equal to 12 g/l. During the drainage and cleaning of the tank three additional lines were assured for delivery of boron solution to the primary circuit and to the spent fuel pool, if necessary. Also measures were taken to prevent possible penetration of clean water to the reactor and spent fuel pool. Nevertheless the operation was outside operational limits and conditions because the emergency boron tank was not available. During the week 22 (25-29 May 1998) the event was investigated by the Bulgarian Nuclear Safety Authority (BNSA). The cases for the SG blow-down pipe rupture are still not clearly identified. Additional control of all similar pipes of all SG's of WWER-440 units at Kozloduy NPP was required by the BNSA. The event was preliminarily rated at level 1 according to the Section III-3.2 of the INES user's manual. After the event investigation the INES level was increased by BNSA to level 2 due to deficiencies of safety culture violation of procedures without justification (Section III-5.3). | PWR | Permanent Shutdown | 440 | 1974 | INES 2 because operations were outside operational limits | 1 |  | 1 |  | H | 1 | 10
928 | 12 | 7 | 2002 | Alto Lucero, Mexico | Mexico | Energy | Plant | LAGUNA VERDE | 1 | 1 | 2 |  | NA | While the reactor was increasing power following inspection and repairing of small leaks in the main steam tunnel, there was an automatic shutdown caused by a failure of the main control personnel to control reactor pressure. During recovery actions, it was found that the Reactor Core Isolation Cooling (RCIC) system was inoperative. Investigation of the incident revealed that the RCIC system had been inoperative for at least a year, because of deficiencies in the surveillance procedures and failure of main control room personnel to detect this condition when this system was required while executing routine activities in July 2001. | BWR | Operational | 805 | 1989 |  | 1 |  | 2 |  | H | 0 | 10
929 | 21 | 11 | 1998 | Alto Lucero, Mexico | Mexico | Energy | Plant | LAGUNA VERDE | 1 | 0 | 2 | 1 | NA | While performing refuelling, at the time of unloading the core and lifting a spent fuel assembly, a failure occurred affecting the refuelling machine which caused the spent fuel assembly to slump to the reactor core. The fuel assembly was taken to a safe condition. Reactor vessel water and refuelling floor atmosphere were monitored without finding any abnormal changes. | BWR | Operational | 805 | 1989 | Basis for rating this event: Event initiator - drop of a fuel assembly; frequency - Low/unlikely; Safety function availability – full. | 0 |  | spent fuel pool |  | T | 0 | 0
930 | 25 | 2 | 1993 | Loviisa, Finland | Finland | Energy | Plant | LOVIISA | 2 | 2 | 2 | 1 | NE | Feedwater pipe rupture during starting up of a feedwater pump. After the pipe rupture, the leakage was rapidly isolated and the operating feedwater pumps stopped. The water levels of the steam generators were controlled by the auxiliary feedwater pumps which started automatically.The pipe rupture occurred at the turbine hall; a few cubic meters of non-radioactive water flowed on the floor of the turbine hall. The reactor was manually tripped before initiation by the automatic protection system. Thereafter, the unit was immediately brought to a stable shutdown condition, and preparations to bring the reactor to a cold shut down condition were started by borating the primary circuit. | PWR | Operational | 526 | 1980 | INES 1 usually assigned to this kind of event - here 2 because of smilar event before | 0 |  | 2 |  | T | 5 | 10
931 | 28 | 5 | 1990 | Loviisa, Finland | Finland | Energy | Plant | LOVIISA | 1 |  | 1 |  | NE | One pipe of the feedwater system of Loviisa 1 broke. The ruptured tube was situated in the turbine hall of the unit. Water and steam flew into the turbine hall. The operation of the Unit was stopped by a manual reactor scram immediately after trip of all feedwater pumps. Both auxiliary feedwater pumps started as planned and the transient in the steam generator level was small. The leak was isolated in about twenty minutes. The local damages to nearby cables and smaller pipelines were significant but no important functions were lost besides the main feedwater system. The leaked water and steam did not include radioactive nuclides. The incident did not endanger the radiation safety at the plant or the environment, and no persons were injured. Investigations have indicated that the wall thickness of the ruptured pipe has been decreased due to erosion corrosion. Also in other four feedwater pipelines at the unit no. 1 as well as in four corresponding lines at the unit no. 2, the erosion corrosion had caused some decrease in the wall thickness. | PWR | Operational | 531 | 1977 |  | 0 | main feedwater system (turbine building) | 2 | erosion corrosion | T | 25 | 40
932 | 26 | 12 | 2004 | Madras, India | India | Energy | Plant | MADRAS | 2 | 2 |  | 2? | A | An earthquake of magnitude 9.1 occurred off the western coast of Sumatra in the Indian Ocean and generated a transoceanic tsunami which devastated the coastline, with a maximum runup of 50.9 m on the northwest coast of Sumatra. When the tsunami struck the plant in India, the condenser cooling pumps were affected due to flooding of the pump house and subsequent submerging of the seawater pumps. Following this, the reactor tripped automatically and the reactor was brought to cold shutdown using the emergency operating procedure. The pump house operating floor is located about 2.5 m above mean sea level, about 2m below the level of the main plant buildings, and is connected by a submarine tunnel about half a kilometre long to the intake well. The increase in water level in the pump house during the tsunami rendered all the seawater pumps located in this area inoperable except for one process seawater pump. This pump was used to cool the NPP’s loads in the initial period following reactor shutdown. Later, this pump also became unserviceable due to clogging of the travelling water screen in the seawater pump house due to the ingress of large quantities of debris from the tsunami. Though off-site power remained available throughout the event, emergency diesel generators were started and were kept running as a precautionary measure. The plant declared an emergency alert at 10:25 on 26 December 2004, which was lifted at 21:43 on 27 December 2004. The tsunami did not affect Unit 2, which was under long shut down. After restoration of the affected areas, the unit was restarted on 1 January 2005. This event showed that external flooding (in particular from tsunamis) can lead to the loss of the ultimate heat sink and create further common cause failures if the flooding level is above the design basis flood. Moreover, it showed that external events can affect simultaneously several units at the same site, and can bring additional issues when the infrastructure is destroyed. | PHWR | Operational | 220 | 1985 | Forerunner to Fukushima but lessons not well learned | 1 |  | 3 |  | T | 1 | 5
933 |  | 3 | 1972 | Oconee, United States | United States | Energy | Plant | OCONEE | 1 | NA |  | NA | NA | Following the first phase of the hot functional testing, an inspection of the reactor coolant system revealed extensive damage to the tube ends and to the tube-sheet welds in the upper head of one of the two steam generators. Cause was found to be loose parts from failed reactor-vessel internal components (in-core instrument nozzels). Of the 52 nozzles, 21 had broken off and 14 had cracks in the region of the weld. In addition, 4 in-core instrument-guide-tube extensions were broken and 4 were cracked. The remaining 44 extensions were intact. Examination revealed that, in addition to the damaged tube ends and tube-sheet welds, the inside surface of the steam generator head had nicks and scratches. | PWR | Operational | 891 | 1973 | precursor to a potentially serious accident - maybe of interest for generic investigations. However, detected prior to commissioning! | 0 | steam generator | 1 | hydraulically induced forces | T | 10 | 100
934 | 12 | 4 | 1991 | Olkiluoto, Finland | Finland | Energy | Plant | OLKILUOTO | 2 | 2 | 2 |  | NE | A fire ignited in switchgear building resulted in a loss of off-site power and reactor scram. All four diesel generators started as planned and all safety features functioned normally. The unit was 8.5 hours without off-site power. The event did not cause any radiation doses or radioactive releases. | BWR | Operational | 910 | 1980 | INES 2 due to long-term loss of off-site power caused by internal fire | 1 |  | 2 |  | Fire | 1 | 10
935 | 1 | 11 | 1996 | Oskarshamn, Sweden | Sweden | Energy | Plant | OSKARSHAMN | 2 | 2 | 2 |  | NE | During periodic testing it was recognised that the core spray pumps were disconnected; the failure was remedied in ten minutes. Two weeks earlier, prior to start up after refuelling, all systems were checked and found o.k.. However, later an additional test was performed when the disconnectors to the pumps were opened and remained so. | BWR | Permanent Shutdown | 661 | 1974 | INES 2 due to degradation of defense in depth | 1 |  | 1 |  | H | 0 | 0
936 | 20 | 11 | 1987 | Oskarshamn, Sweden | Sweden | Energy | Plant | OSKARSHAMN | 3 | ?0 | 2 |  | NE | Criticality shut down margin experiment started without hydraulic scram system being operable | BWR | Operational | 1450 | 1985 | INES 2 probably due to degradation of defence-in-depth and deficiencies in testing procedures | 1 |  | 1 |  | H/T (?) | 0 | 0
937 | 20 | 8 | 1997 | Paks, Hungary | Hungary | Energy | Plant | PAKS | 3 | 2 | 2 |  | EE | On 20 August at 02:30 tests of the modified turbine controller were being carried out and for this reason three out of six main coolant pumps were switched off. Reloading of the reactor and the turbines occurred as expected. At 02:33 unexpected level increase in one of the six steam generators (SG) was observed. The level increase continued though the level interlock actuated properly and operator action was carried out. At 02:37 unit protection on high SG level actuated that caused the trip of both operating turbines. During the reactor protection actuation sticking of one of the 37 control rods was identified in a position about 25-50 cm from the upper end position. The parameters of the reactor were stabilized. The cause of the SG level increase has not yet been identified; for defining the causes of the control rod sticking elaboration of a programme was started. Cooling down of the reactor was initiated. On 7 August 1997 sticking of the same control rod was identified during starting the reactor after annual outage. That time the sticking was eliminated with repeated operation of the rod. During additional tests of the affected rod the failure did not reoccur, the reactor was restarted. | PWR | Operational | 500 | 1986 | INES 2 due to repetition of sticking of one control rod | 1 |  | 1 |  | T | 0 | 10
939 | 30 | 6 | 1988 | Paks, Hungary | Hungary | Energy | Plant | PAKS | 4 |  | 1 |  | EE | Refuelling of Unit 4 was commenced on 18 June 1988. Operating personnel performed a planned switchover to natural circulation from loops 4 and 6 to loops 1 and 3 on 30 June. Meanwhile, the effectiveness of core cooling by natural circulation decreased sharply for about a 3 hour period. After switching over the natural circulation among the llps, the operating personnel isolated loops 4 and 6 and started to drain them. Nitrogen used to drain the water got into the loops in operation and most of the water was pushed from the SG primary side into the reactor vessel. The operator tried to stop disturbance of natural circulation by starting periodically the make-up pump to the working loops. During this injection the personnel performed venting several times to take away the gas-air mixture from the top of SG headers, Eventually, restoration of natural circulation was achieved by continuous venting of the SG headers. | PWR | Operational | 500 | 1987 |  | 1 | Natural circulation core cooling | 1 |  | ? | 0 | 0
940 | 20 | 1 | 1993 | Paluel, France | France | Energy | Plant | PALUEL | 2 | 1 | 2 |  | WE | A periodic test of the steam generator auxiliary feedwater system, combined with the presence of a steam valve which had failed to close fully, brought about a hence overrapid cooling of the reactor coolant system. The operator took immediate action to bring the reactor back to zero power and decided to inhibit the safety injection automatic triggering devices and the steam isolation devices, which he deemed to be useless in the circumstances. | PWR | Operational | 1382 | 1984 | Level 2 on the French severity scale due to inhibition of safeguard actions without sufficient justification | 1 |  | 2 |  | H | 0 | 10
941 | 1 | 10 | 1990 | Paluel, France | France | Energy | Plant | PALUEL | 1 | 2 | 2 |  | WE | An inspector of the regulatory body detected that filters of the water sump on the containment building were not properly installed to prevent safety pumps from sucking debris. This system is expected to (re-)inject cooling water to the reactor core after a major rupture of primary piping. All the 1300 MW(e) reactors are at present being brought into line with accepted standards. | PWR | Operational | 1382 | 1984 | Level 2 of the French severity scale not justified - probably due to long-term degradation of a safety function | 1 |  | 1 |  | T/H | 1 | 20
942 | 14 | 8 | 2003 | Pickering, Canada | Canada | Energy | Plant | PICKERING | 1,2,3,4,5,6,7,8 | ?2 | 2 |  | NA | All eight reactor units at Pickering A and B experienced a total loss of the on-site electric power, caused by a blackout that affected the electric grid supplying the Province of Ontario, Canada, and parts of the US. At the time of the event, Pickering A had units 1, 2 and 3 in the guaranteed shutdown state and unit 4 running at 12% of full power but not synchronized to the grid. Pickering B station had units 5, 6 and 8 operating at full power while unit 7 was heating up as it returned to service from a planned outage. All operating units were safely shutdown. However, for a period of approximately 5.5 hours, immediately following the blackout, cooling of the reactor units was achieved only by natural circulation. Additionally, the High Pressure Emergency Coolant Injection (HPECI) System (common to all units) which is required to protect the hot-shutdown or operating units against accidents, if certain failures were to occur, was impaired. Units in the guaranteed shutdown state did not require the protection of the HPECI System. Another back-up heat sink, the Shutdown Cooling System, was also unavailable for 3 hours. At all times, on all units, reactor power was controlled, fuel was adequately cooled and containment was available. | PHWR | Operational;Permanent Shutdown;Permanent Shutdown;Operational;Operational;Operational;Operational;Operational | 542;542;542;542;540;540;540;540 | 1971;1971;1972;1973;1982;1983;1984;1986 | INES 2 adequate for units in operation, interesting precursor - event controlled safely | 1 |  | 3 |  | T | 30 | 50
943 | 4 | 10 | 1996 | Saint John, Canada | Canada | Energy | Plant | POINT LEPREAU | Single | 2 | 2 |  | NA | The reactor was shutdown on 29-09 to inspect the secondary side of Boiler #3 to determine the cause of level disturbance anomalies. Entry to the affected boiler into the area of the Emergency Water Supply/Reheater Drains Distribution Header was made on 04-10. During the inspection, it was discovered that the header had severe erosion/corrosion damage. Through wall holes in the header were found at the tee connection, and the sleeve connection at the shroud was displaced and damaged. Consequently, a decision was made to inspect the headers in all boilers and similar damage was found in each boiler. The headers in all boilers were removed and replaced with an erosion/corrosion resistant material. It was subsequently assessed that the boilers were fit for service as no other damage affecting structural integrity was observed. The defective headers were assessed as not being related to the boiler level indication anomalies. Following completion of this work the reactor was returned to operation. | PHWR | Operational | 705 | 1982 | INES 2 due to degradation of defense in depth and inadequate surveillance program | 1 |  | 1 |  | T | 0 | 1
944 | 31 | 5 | 1991 | Saint John, Canada | Canada | Energy | Plant | POINT LEPREAU | Single | 2 | 2 |  | NA | During routine calibration of the Regional Overpower (ROP) detectors for Shutdown System 1 and 2, an incorrect calibration factor was applied. The calibration factor used was applicable for operation at 96%, however, the reactor was at 100% full power. This error in calibration was discovered approximately six hours later at which time all detectors were recalibrated to the correct value. The calibration error was in the unsafe direction, therefore, the rip effectiveness on this parameter for both shutdown systems was reduced for the period which the incorrect calibration existed. | PHWR | Operational | 705 | 1982 | INES 2 due to degradation of defence-in-depth | 1 |  | 1 |  | H | 0 | 0
945 | 27 | 9 | 1997 | Ringhals, Sweden | Sweden | Energy | Plant | RINGHALS | 4 | 1 | 2 |  | NE | During start-up procedures while the reactor temperatures were still far below operational values it was detected that the valves at the containment spray pump' suction were closed in contrary with their required open position. The testing instructions were not clear. A similar event occurred recently at unit 2. | PWR | Operational | 1171 | 1982 | INES 2 probably due to degradation of safety function | 0 |  | 1 |  | H | 3 | 4
946 | 3 | 10 | 1994 | Ringhals, Sweden | Sweden | Energy | Plant | RINGHALS | 2 | 2 | 2 |  | NE | A scram occurred due to a failure of a condensate pump. Analyses of the pressure versus time charts shows that during a few minutes the secondary pressure reached almost 110% of the permitted value. It is therefore questionable whether the valves pressure release function is fulfilling specifications. A reason for the failure is that the conversion factor from compressed air to steam was erroneously calculated, corresponding to less than 10% higher opening pressure (valid also for Ringhals 3 and 4). | PWR | Operational | 963 | 1974 | INES 2 due to degradation of defense in depth | 1 |  | 2 |  | H (wrong calculations) | 0 | 10
947 | 14 | 3 | 1971 | Hartsville, United States | United States | Energy | Plant | ROBINSON | 2 | 2 |  | 1 | NA | Workman turned on an emergency oil pump, powered by the dc supply, for a weekly 2-hr test run and then forgot to turn it off. About 4 hr after the oil pump had been turned on, the reactor scrammed. However, by this time the voltage from the dc electrical supply system had become too low, which caused several auxiliary electrical circuits to fail. All eight turbine and generator bearings suffered some damage. Primary-coolant-pump shaft warped and had to be replaced. Two months to repair damage. No injuries and no radioactivity released. | PWR | Operational | 780 | 1970 |  | 1 |  | 2 |  | H | 70 | 150
948 | 17 | 9 | 2010 | Busan & Ulsan, South Korea | South Korea | Energy | Plant | SHIN-KORI | 1 | 1 | 2 |  | A | Inadvertent Containment Spray of Reactor Coolant. licensed by the Government (Ministry of Education, Science and Technology) on May 19, 2010, under power ascension test at 50% power, was manually shutdown on September 14, 2010 to re-adjust the ex-core detector position. After completion of the maintenance for the ex-core detector, the plant restarted the heat-up operation controlling the reactor coolant temperature utilizing the shutdown cooling system; the plant was on mode 4 with the RCS pressure and temperature was 28kg/cm2 and 145℃, respectively. Both the shutdown cooling system and the containment spray system share the shutdown heat exchanger and are separated by the heat exchanger outlet isolation valve (CSV033) and the containment spray isolation valve (CS-V035). CS-V033 was opened and CS-V035 was closed when the incident occurred. On September 17, at 14:17, the CS-V035 opened inadvertently due to a human error, and reactor coolant was sprayed into the containment through the containment spray system. The RCS experienced a severe transient; the pressure was decreased rapidly from 28kg/cm2 to 3.9kg/cm2 and the temperature and water level were lowered quickly. Rapid decrease of RCS pressure and water level was identified by the MCR operators, and the operators carried out responsive actions in accordance with the emergency operating procedure (EOP) including stop of reactor coolant pumps (RCPs), isolation of the letdown line, and increasing the charging flow. Also, additional safety measures were taken; manual actuation of the safety injection to recover the RCS inventory, and manual actuation of containment isolation to prevent radioactive material release to the environment. After taking a series of initial responses, MCR operators identified that the containment spray isolation valve (CS-V035) was abnormally opened; the valve was manually closed at 14:54 and the plant entered into stable condition. The result of analyses based on the changes of refueling water tank (RWT) level and RCS inventory showed that the amount of the sprayed water (or borated water) to the containment was 423 tons. During the event progression, major plant safety systems including the emergency diesel generator (EDG) and containment purge isolation were actuated as designed. As a result of the event, most of the Structures, Systems, Components (SSCs) inside the containment were affected by the sprayed borated water; especially the reactor cavity and the containment floor level were flooded. As the operating parameters such as leakage rate of reactor coolant was within the emergency issuance condition, the plant declared emergency (Alert level) at 15:00, and cleared at 18:00 after confirming the plant operating conditions. | PWR | Operational | 1044 | 2010 | Root Causes and Corrective Actions Inadvertent opening of CS-V035 occurred due to the human error mixed with (1) MCR operator's mishandling of the CS-V035 hand-switch and (2) test engineer's local equipment manipulation without approval of the MCR, which directly caused the spray of borated water to the containment. In detail, acknowledging that the thermal overload relay tested on the previous day was not reset after the test, test engineer pressed the “RESET” button installed at the local breaker to make it clear possible and it led to the opening of CS-V035 which already had erroneous opening signal by MCR operator’s mishandling of the CS-V035 hand-switch. Though there were some design changes for the containment spray system compared to the reference plant (Ulchin Unit 5 and 6 of Korea), those were not reflected into the operating procedure; the shutdown heat exchanger outlet isolation valve (CS-V033), the up-stream of CS-V035, (which should be closed during the heat-up operation) had been opened, which contributed to the event occurrence as one of the root causes. Additionally, inappropriate organization attitude toward plant commissioning was also another causal factor | ? |  | 1 |  | H | 50 | 70
949 | 22 | 7 | 1991 | Desnogorsk, USSR_Russia | USSR_Russia | Energy | Plant | SMOLENSK | 2 | 1 | 3 |  | EE | On completion of unit preventive maintenance testing and adjustment of Main Safety Valves (MSVs) was in progress. Four MSVs have been tested in turn, and only one pilot valve (PV) functioned as designed. The remaining PVs failed to completely close (remotely) and were giving oil steam. This led to pressure increase in the sealed rooms up to the setpoint of AZ-5 emergency protection actuation and a maximum design-basis accidentv (MDBA) signal was formed in the protection systems logic. Group 1 hydrovolumes of Emergency Core Cooling System (ECCS) were activated. The mechanisms of ECCS subsystems 1,2 and 3 failed to adequately respond to the design algorithm. 7 mins. after the MDBA signal was formed in the 2nd set of protections logic, the same signal was generated in the 1st set. The mechanisms of ECCS subsystem 1 started and functioned according to the design algorithm while ECCS subsystems 2 and 3 failed to respond. Subsequently the primary circuit was being cooled down by personnel at a rate specified by procedure. Safety function availability - adequate. | LWGR | Operational | 1000 | 1985 | INES 3 due to operational procedure and safety culture deficiencies | 1 |  | 1 |  | T/H | 1 | 90
950 | 22 | 7 | 1990 | Desnogorsk, USSR_Russia | USSR_Russia | Energy | Plant | SMOLENSK | 2 |  | 1 |  | EE | While testing automatic activation of 6 kV auxiliary power bus standby source of Unit 1 which was in maintenance and due to switching overvoltages, standby boiler's 6 kV cable insulation was damaged resulting in cable short-circuiting and burning. This resulted in the damage to Unit 2 cables laid nearby, deenergizing of two 6 kV auxiliary power buses, loss of power to two reactor coolant pumps causing the actuation of reactor scram. Breach of safe operation limits and conditions did not occur. Radiation situation remained normal. No injuries occurred while extinguishing the fire. Intitial event - cable burning. Event expected, real. Safety function availability: full. Table 1: A-1R - level 0/1. It was found that the non-design cable was used. Units 1 and 2 cables were laid together which constitutes violation of procedure, therefore level 1 has been chosen. | LWGR | Operational | 1000 | 1985 |  | ? | Power supply: 6 kV auxiliary power buses | 2? | Non conforming installation | H | 0 | 10
951 | 22 | 8 | 1997 | Nikolaev oblast, Ukraine | Ukraine | Energy | Plant | SOUTH UKRAINE | 2 | 0 | 2 |  | EE | During the planned outage, refuelling is in progress. After loading a fresh assembly into the core, refuelling machine (RM) operator pulled out RM beam from the reactor and started to relocate RM to spent fuel pool area in order to take the next fresh fuel assembly. While RM was moving, personnel heard unusual noise and stopped RM. A damaged fresh fuel assembly was found on RM beam in spite of the fact that according to all instrumentation readings, the assembly had been left in the core. The damaged fuel assembly was removed out of RM, no personnel overexposure and radioactive releases occurred. | PWR | Operational | 1000 | 1985 | INES 2 due to degradation of defense in depth | 1 |  | 1 |  | T | 0 | 1
952 | 6 | 4 | 1994 | Nikolaev oblast, Ukraine | Ukraine | Energy | Plant | SOUTH UKRAINE | 1 | 2 | 2 |  | EE | During the routine walkdown the operating staff registered not authentic readings of the steam generator no. 3 level controller connected to the emergency protection system circuit. Safety operation conditions of the Technical Specifications which allow corrective measures within 8 hours were violated, actually the defect has been eliminated in 14 hours. | PWR | Operational | 1000 | 1982 | INES 2 due unjustified violation of technical specifications and not timely elimination of the defect | 1 |  | 1 |  | H | 0 | 1
953 | 21 | 9 | 1992 | Nikolaev oblast, Ukraine | Ukraine | Energy | Plant | SOUTH UKRAINE | 1 | 1 | 2 |  | EE | Unit was restarted after planned maintenance and was gaining power. At the power level of 450 MWe (at 7:52 a.m.) the reactor was shut down by the emergency protective system on neutron flux level actuation. The actuating signal had been formed as a result of a defect in the reactor neutron flux control system elements. During the transient process, because of the failure of the fast-acting isolating valves of the steam pipe (protective systems affecting valves were not in preparedness state), there was a pressure drop in the steam generators and of the level in the pressurizer lower than the prescribed limits for safe operation. | PWR | Operational | 1000 | 1982 | Unfortunately info is missing on how the event proceeded - hopefully safety systems and oper ator worked well | 1 |  | 1 |  | T | 0 | 10
954 | 1 | 12 | 1990 | Nikolaev oblast, USSR_Ukraine | USSR_Ukraine | Energy | Plant | SOUTH UKRAINE | 1 | 1 | 2 |  | EE | Safety System (SS) train 3 diesel generator (DG) started on 6 kV bus deenergization. This was followed by DG trip by the maximum current protection of its excitation system. After connecting the essential bus to the service bus and following unsuccessful attempt to start the service water pumps for essential consumers damage to manway hatch of the service water system was discovered. The essential bus deenergiztion was caused by the short circuit in the "redundant complex" cable provided for by initial design and later disconnected from one end only. SS trains 1 and 2 testing was performed on time. 16 hours 55 min later SS train 3 was successfully tested with sequential loading. During the event the unit was operating at 760 MWe power. BASIS FOR RATING: Initiator - expected, real (essential bus deenergization). Safety function availability - within limits and conditions. According to Table A2 - level 1/2 (B-1R). Level 2 has been chosen since the event reveals safety culture deficiencies. | PWR | Operational | 1000 | 1982 | INES 2 due to safety culture deficiencies | 1 |  | 1 |  | H | 0 | 1
955 | 11 | 10 | 1992 | Saint-Maurice-l'Exil, France | France | Energy | Plant | ST. ALBAN | 1 | 0 | 2 |  | WE | Inspections during the maintenance and refueling shutdown revealed more than 200 metallurgical defects, not complying with the construciton rules, on the main steam pipes of the secondary system of the installation. | PWR | Operational | 1381 | 1985 | INES 2 because the defects may cause main steam line rupture (with low probability) | 0 |  | 2 |  | T | 1 | 10
956 |  | 11 | 1973 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 1 | 2 |  | 1 | NA | Operator noted a reduction of water flow from one of the primary coolant pumps, accompanied by excessive vibration in the same pump. He initiated a controlled shutdown of the reactor. When the power level had dropped to 40% of power, an automatic scram was set off by the complete loss of flow from the pump as the pump shaft had broken. An examination revealed that the break had occurred at a place where the shaft diameter was reduced. The radius machined in this area was too small, resulting in excess stress. The shafts of all main reactor coolant pumps were replaced with shafts of a different design, and the reactor was returned to service. | PWR | Operational | 890 | 1972 | Incident resulted in damage to major equipment – clearly no contribution to CCDP. Fabrication error. | 0 |  | 1 |  | T | 1 | 10
957 | 4 | 7 | 2005 | Tihange, Belgium | Belgium | Energy | Plant | TIHANGE | 2 | 0 | 2 |  | WE | Inadequate protection relays and related setpoints. During periodic testing of the diesel generators automatic load sequence, it was discovered that the 380V safety related equipments were not energized as expected. The reason for that failure is that a protection relay had an unexpected high voltage trip value that was not appropriately adjusted. The setpoint was too low so that, when the diesel generator was supplying the 380 V board, the protection tripped on high voltage de-energizing power supply to safety related equipments. At the same time, it was discovered that the low voltage setpoint was not adjusted as by the design specification and that it was not possible to reach the right value due to construction features of the protection relay. Some of these safety related 380 V boards were replaced during the last plant outage in April 2005 and all the new boards had the same problem, having the same inadequate protection relay. The consequence was that some of the safety related equipments were not available in two out of three safety related trains in case of loss of off-site power supply. The same problem was also present in one train of the second level protection systems (plant protection against external events). After identification of the problem the license immediately re-adjusted the high voltage setpoint to a higher value. The adjustment of the low voltage setpoint is under investigation. | PWR | Operational | 1055 | 1982 | unidentified inoperability of emergency power supply during plant operation until revision | 1 |  | 1 |  | H | 0 | 0
958 | 24 | 11 | 2000 | Pierrelatte, France | France | Energy | Plant | TRICASTIN | 3 | 1 | 2 |  | WE | Four successive events (error in piping alignment, valve position and pump operation, Emergency Core Cooling System unavailability) occurred between 21 and 24 November during restart stages. These incidents are mainly relying on human and organisational factors. Each of these events would be rated, at the most, at level 1 on the INES scale. However, their accumulation within a very short period, significant of a collective lack of rigor, led the Nuclear Safety Authority to rate the last of them at level 2 on the INES Scale. | PWR | Operational | 955 | 1981 | INES 2 due to accumulation within a short period of time and collective lack of rigor | 1 |  | 1 |  | H | 0 | 0
959 | 22 | 8 | 1990 | Pierrelatte, France | France | Energy | Plant | TRICASTIN | 1,2 | ?2 | 2 |  | WE | The sand filters installed in 1988 to decrease pressure within containment buildings in case of a hypothetical severe accident were found to have been inoperable for one year due to abnormal presence of plugs in the pipes leading to the sand filters shared by the two units. | PWR | Operational | 955 | 1980 | Level 2 of the French severity scale not justified - probably due to long-term degradation of a safety function | 1 |  | 1 |  | H | 0 | 10
960 | 31 | 1 | 1992 | Trillo, Spain | Spain | Energy | Plant | TRILLO | 1 | 2 | 2 |  | WE | During staff investigation of a minor event the staff detected a design error in the level instrumentation in the annulus between the sphere and the containment building, affecting 3 out of 4 sumps. This error, deficiency in 3 sumps, would have affected the actuation of Residual Heat Removal System (RHR) during a small LOCA, in the recirculation phase and would have resulted in inadequate safety function. This deficiency has been present since the start-up of the plant. The error has been corrected and the plant is operating at full power. | PWR | Operational | 1066 | 1988 | INES 2 without justification - probably due to long lasting impairment of safety function | 1 |  | 1 |  | H (design) | 0 | 1
961 |  | 6 | 1987 | Prescott, United States | United States | Energy | Plant | TROJAN | Single | 2 |  | 0 | NA | Significant unexpected erosion of main feedwater(MFW) lines caused by flow accelerated corrosion (FAC); degradation of those was discovered by the licensee in at least two areas of the straight sections of ASME Class 2 safety­related MFW piping inside containment. The thinning was discovered when the Trojan steam piping inspection program was expanded to include single­phase piping. The thinning was attributed to high fluid flow velocities and other operating factors. | PWR | Permanent Shutdown | 1155 | 1975 | secondary - technical - no degradation of safety function - omit (?) | 0 |  | 2 |  | T | 1 | 10
962 | 24 | 8 | 1992 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3,4 | 2 |  | 2 | NA | Hurricane Andrew passed directly over the two-unit nuclear power station just south of Miami with a sustained wind speed of 145 mph and gusts of at least 175 mph. The plant lost all offsite power during the storm and the following five days. Emergency diesel generators provided onsite power and maintained the plant during recovery operations until offsite power was restored 6 days later. All offsite communications were lost for 4-hours during the storm and access to the site was blocked by debris and fallen trees. The nuclear power station’s fire protection system was destroyed when winds and wind-generated missiles toppled a tower supporting a water storage tank containing 100,000 gallons of water used for fire fighting; fire suppression system was declared inoperable prompting a station “Alert” to be declared. Following the storm, pumps and hoses were deployed to a near-by salt water lagoon to compensate for the loss of the fire suppression system. The nuclear power station is one of the few US reactors with electrical power cables used for shutting down the reactor installed on the exterior of the reactor containment buildings. These cable trays and conduits were coated with a fire-resistant material. The hurricane forcewinds stripped much of the fire resistant coating off these exterior applications exposing the reactor shutdown cabling to any subsequent fire. The wind blew the combustible fuel from the two adjacent oil fired plants over the nuclear site as well as an oil slick over the lagoon later designated the source for backup fire suppression water inventory. Fortunately the fuel oil did not ignite with the passing storm. | PWR | Operational | 829 | 1972;1973 | external - degradation of power supply/safety function - interesting precursor | 1 |  | 3 |  | T | 221 | 237
963 |  |  | 1971 | Florida City, United States | United States | Energy | Plant | TURKEY POINT | 3 | 1 |  | 0 | NA | During hot functional testing (prior to fuel loading and start of operation), three of four safety valves suddenly separated from two headers of a main steam line in the secondary system. Substantial rule changes were adopted as a result of this incident. The nuclear system was not involved in this incident; no release of radioactivity. | PWR | Operational | 829 | 1972 |  | 0 |  | 2 |  | H | 0 | 1
964 | 25 | 8 | 2004 | Vandellos, Spain | Spain | Energy | Plant | VANDELLOS | 2 | ?0 | 2 |  | WE | With train A of the Emergency Service Water (ESW) in service, train B of the ESW was started up in order to proceed with the reparation of a check valve and replace a flow meter. At the impulsion side of train B an immediate drop of pressure was detected after the pump was started up, what led the crew to stop the pump and proceed to investigate the event. After checking it locally, a break was found in the hatch neck , located in a small chest after the pumps building. After reparation and restoring operability of train B, plant personnel proceeded to inspect train A of the ESW. Similar loss of thickness due to corrosion was found at the same hatch neck as the repaired one in train B and similar reparation was conducted in train A. The remaining hatch necks showed thickness within the engineering margins, although some of them presented corrosion points. Afterwards, it has been revealed that the utility was aware of the degradation of train A almost simultaneously to the degradation of train B since 1993 but maintenance activities had not been improved. In year 2000 no measures were taken after an inspection report had recommended an measure of the thickness of the affected hatch neck. May, the 10th 2004 percolated dampness was identified and the utility did not declare the correspondent “non-compliance” status of the plant. | PWR | Operational | 1087 | 1987 | INES 2 due to lack of safety culture | 0 |  | 2 |  | T | 7 | 10
965 | 27 | 11 | 1999 | Killona, United States | United States | Energy | Plant | WATERFORD | 3 | 0 | 2 |  | NA | With the unit shut down and reactor coolant system (RCS) at 146 C and 2,413 kPa, plant operators were preapring to place one train of shutdown cooling into service. When they opened the motor-operated suction valve for the "B" low pressure safety injection pump, indicated pressurizer level decreased from 35% to offscale low, and RCS pressure decreased to 689 kPa. Operators closed the pump suction valve to terminate the coolant loss, and tripped the operating reactor coolant pumps due to low RCS pressure. Approximately 20,818 litres of coolant flowed from the RCS to the refueling water storage pool. Pressurizer level was restored after operators manually started one of the high pressure safety injection pumps. The licensee declared an ALERT emergency classification due to this event. | PWR | Operational | 1250 | 1985 |  | 1 |  | 1 |  | H | 0 | 1
966 | 17 | 6 | 2014 | Gyeongju-si, South Korea | South Korea | Energy | Plant | WOLSONG | 4 | 0 | 1 |  | A | During an overhaul, a fine crack was found at the pipe junction on the pressurizer side of the steam relief valve. Upon investigation, it was identified that thermal load was repeated by steam relief valve actuation in condition that connected pipe was stuck due to defective construction of supporting structure and, therefore, the crack was caused by corrosion fatigue crack at the weld. | PHWR | Operational | 656 | 1999 |  | ? |  | 1 |  | T | 0 | 1
967 | 3 | 9 | 2009 | Gyeongju-si, South Korea | South Korea | Energy | Plant | WOLSONG | 2 | 0 | 1 |  | A | During the annual overhaul, while performing a surveillance test for the Current Transformer (CT) of the main generator on September 3, 2009, Wolsong Unit 2 experienced a Loss of Voltage (LOV) at the safety bus due to opening of the switchyard breaker(Power Circuit Breaker 7300). The switchyard breaker was opened inadvertently due to spurious actuation of the ‘reverse power relay (32A relay)’. In response to the LOV, the Standby Diesel Generator (SDG) #2 started up automatically and the safety related equipments loaded from the SDG were actuated automatically and successfully as designed. However, the SDG #1 did not started up because it was under maintenance. The safety grade-4 power (13.8 kV) could be restored by closing the Power Circuit Breaker (PCB) 7300, 33 minutes after the LOV while implementing the Emergency Operating Procedure-015 (Loss of Grade-4 Power). Upon investigation, the reverse power relay was found to be actuated due to several factors such as 1) unanticipated performance of the circuit containing the protective relay (78 relay, out-of-stop relay) and the reverse power relay, 2) the plant operator’s failure to confirm the plant initial condition for surveillance and 3) improper process control for the annual overhaul work. After the LOV which continued 17 seconds for the train-B and 33 minutes for the train- A, the SDG #2 automatically actuated and it supplied power to the train-B and the train-A power was restored by closing the PCB 7300. While restoring the LOV condition and implementing the EOP, there was no problem with the safety function and the plant was maintained in the guaranteed shutdown condition. Causes and Corrective Actions During the reconstruction test, it was found that an unanticipated 190 mV voltage for 78Ry and 108 mA current for 32A was generated in the circuit (Fig. 2) by opening and closing the ‘knife switch’ during measurement of the CT insulation resistance. And the unanticipated generatedcurrent again caused the protective relay (32A) to actuate of which the setpoint was 45 mA. According to the overhaul schedule, while performing the CT surveillance test, the PCB 7300 should be in open position, the main transformer should be in shutdown mode and the link (generator output breaker) should be disconnected from the generator. However, the PCB 7300 was in closed position and the main transformer was pressurized during the surveillance test. Accordingly, this event was attributed to spurious actuating of the 32A relay which the operators couldn’t anticipated and the improper process control for the maintenance work. The following corrective actions were implemented. - Revised the related surveillance and maintenance procedures - Improved the process control for the overhaul work - Planed to improve the Out-of-Stop Relay (long-term plan) Safety Assessment Safety related variables i.e., the reactor header inlet/outlet temperatures, the moderator outlet temperature, the component cooling water (CCW) temperature and the spent fuel pool temperatures were checked in depth. And the reactor coolant system (RCS) subcooling was identified to be maintained, the CCW temperature was found to be increased from 25 ℃ to 34 ℃ which was below the limit value, 38 ℃. There was no adverse effect on the plant safety or radioactive material release to the environment as a result of this event. | PHWR | Operational | 655 | 1997 |  | ? |  | 3 |  | T | 0 | 0
968 | 6 | 11 | 2005 | Gyeongju-si, South Korea | South Korea | Energy | Plant | WOLSONG | 1 | 2 | 1 |  | A | During its 91.5% reactor power, the "reactor containment box-up" occurred which caused the 40 isolation valves of the reactor ventilation system to close. Upon investigation, the sequence of box-up event was like this; a fault sprinkler nozzle of the D/G room adjacent to the "secondary control area(SCA)" discharged water, the sprinkled water penetrated inside the panel of the SCA and the water penetration into the SCA panel caused a spurious signal. As a result of the sprinkler nozzle failure in the #2 D/G room and the sprinkled water, the radiation monitoring panel, the #2 D/G panel and other panels in the SCA were partially submerged. The utility implemented a replacement of the damaged components with spare parts(radiation monitoring panel), integrity inspection(SCA panels) and disassembly inspection for the #2 D/G. The reactor containment box-up signal from the SCA panel is different from the reactor trip signal and do not cause subsequent reactor trip or power reduction. Confirming the integrities of components and proper measures for the box-up signal, the box-up was cleared at 7:33 a.m. on Nov. 6, 2005. During the box-up event, all plant safety systems operated as expected and there was no radiation release to the site nor to the environment. | PHWR | Operational | 682 | 1982 |  | 0 |  | 1 |  | T | 0 | 1
969 | 20 | 10 | 1994 | Gyeongju-si, South Korea | South Korea | Energy | Plant | WOLSONG | 1 | 2 | 2 |  | A | Opening of one of the four Coolant Liquid Release Valves in the Primary Heat Transport System (PHTS), due to its actuator failure, while the reactor was operating at full power. Heavy water in PHTS was released to the degasser condenser. The reactor automatically tripped on pressurizer low level about two minutes later. The turbine runback was initiated, and the operator manually tripped the turbine. Degasser condenser pressure control spray valves and level control valves were closed as designed. PHTS pressure recovered and stabilized with one liquid relief valve open. Operator action was focused on keeping the coolant inventory in the pressurizer and the feed pump suction head by pumping heavy water from the supply tank to the storage tank, while maintenance crew investigated the cause of the problem and the possibility of repairing the damaged liquid relief valve. The cooldown and the depressurization was not performed by the operator immediately. Degasser condenser pressure was built up due to heavy water inflow through the small line connected to the feed water pump discharge. This caused both degasser condenser relief valves to open and heavy water to spill onto the floor sump. Steaming of hot water caused reactor building isolation on reactor building pressure high signal for a few minutes. The operator cooled down the reactor and depressurized PHTS. During the event about 6.5 tonnes of heavy water were spilled. There was no notable radiation exposure and radioactivity release to the environment. | PHWR | Operational | 682 | 1982 | INES 2 probably due to spill of radioactive heavy water to the sump floor and delayed operator action (the degasser condenser relief valves opening resulted from the operator's delayed-action for plant cooldown and depressurization) The root cause of the reactor trip was the crack of a diaphragm of the liquid relief valve and the cause of heavy water spillage to the sump floor through the degasser condenser relief valves was the operator's delayed- action for plant cooldown and depressurization. The following actions were taken after this event : - Reviewed and reestablished diaphragm replacement programs for all air operated valves. - Revised emergency operating procedures corresponding to liquid relief valve failures in order to prevent the degasser condenser relief valve from lifting. This includes early decisions regarding PHTS cooldown and depressurization. | 1 |  | 1 |  | T;H | 4 | 6
970 |  | 11 | 1984 | Gyeongju-si, South Korea | South Korea | Energy | Plant | WOLSONG | 1 | ? |  | 1 | A | One of the two air operated Liquid Relief Valves (LRV) on each of the two primary heat transfer (PHT) loops opened spuriously partially filling the degasser-condenser and initiating a small LOCA through the rupture discs of the heavy water storage tank (HWST). About 25 tonnes of heavy water (nearly 13 percent of core inventory) was lost from the PHT system during this event that was terminated 20 minutes later by replacing the fuse that was damaged before during checks by a control technician. | PHWR | Operational | 682 | 1982 | primary, human (maintenance) | 1 |  | 1 |  | H | 0 | 10
971 | 23 | 1 | 1991 | Enerhodar, USSR_Ukraine | USSR_Ukraine | Energy | Plant | ZAPOROZHYE | 1 | 1 | 2 |  | EE | The unit was shut down by operating personnel due to breach of normal operation condition, namely, the time of safety system (SS) train 3 diesel generator being removed from service in excess of that specified by procedure. DG-3 tripping occurred during routine test of SS train 3 components immediately after connection to the bus. The cause of DG-3 trip is breaker defect. During replacement of the DG's faulty breaker the subsitute breaker designed for transformer switchings was erroneously installed. The closure of this breaker resulted in the damage to DG-3 exciter. BASIS FOR RATING: Event - postulated, expected (failure of one SS train while routine testing). Safety funciton availability - adequate. According to Table A1 - level 1/2 (C-1P). Level 2 has been chosen since the event revals safety culture deficiencies. | PWR | Operational | 1000 | 1984 | INES 2 due to safety culture deficiencies | 1 |  | 1 |  | T/H | 0 | 10
972 | 2 | 10 | 1991 | Enerhodar, Ukraine | Ukraine | Energy | Plant | ZAPOROZHYE | 2 | 0 | 2 |  | EE | During replacement of generator exciter anchor, due to alignment errors at the special water treatment facility in the auxiliary building contaminated water got into the secondary circuit (deaerators, etc.). Increased activity as compared to that specified in the procedure was detected only in deaerators and secondary side of the steam generator slightly above the authorized value - 2E-8 Ci/l); radiation situation in the turbine building remained within background values. Radioactivity release to environment, contamination of the buildings, rooms and personnel overexposure did not occur. | PWR | Operational | 1000 | 1985 | INES 2 due to safety culture deficiencies | 0 |  | 2 |  | H | 0 | 1
973 | 30 | 12 | 1991 | Enerhodar, Ukraine | Ukraine | Energy | Plant | ZAPOROZHYE | 2 | 2 | 2 |  | EE | Spurious activation of fire extinguishing system occurred in one of the plant rooms. The water from the affected room penetrated to the lower room onto the Engineered Safety Feature Actuation System (ESFAS) panels of Safety System (SS) - 1 which resulted in the actuation of that train. In the course of the load sequencing that followed, the valves on the discharge from the spray pump to containment room opened; then the spray pump was tripped by control key. Alarm indication showed the open steam generator-1 pilot valve (PORV). After unsuccessful attempt to close this valve using control key, the Reactor Coolant Pump (RCP) -1 was tripped and the unit power was reduced to 67%. Due to water spilling onto the ESFAS cabinets the diesel generator-1 tripped and the essential bus was deenergized. The reactor was then brought to subcritical condition using the PZ-1 (emergency protection) button. | PWR | Operational | 1000 | 1985 | INES 2 due to safety culture deficiencies (untimely testing of remaining two SS trains (?)) | 1 |  | 1 |  | T | 0 | 10
974 | 19 | 5 | 1996 | Pope, United States | United States | Energy | Plant | ANO | 1 | ? |  | 1 | NA | Reactor Trip and Subsequent Steam Generator Dryout | PWR | Operational | 903 | 1974 |  | 1 | Main Feed Water (MFW) pump, Main Steam Safety Valve (MSSV) | 2 |  | T | 8 | 12
975 | 1 | 11 | 2006 | Southport, United States | United States | Energy | Plant | BRUNSWICK | 2 | ? |  | 1 | NA | Loss of startup auxiliary transformer results in Unit 2 manual reactor protection system actuation. | BWR | Operational | 960 | 1975 |  | 1 | Power supply: Startup Auxiliary Transformer | 2? | ineffective mechanical connection; inadequate predictive maintenance | T;H | 25 | 35
977 | 18 | 2 | 2010 | Lusby, United States | United States | Energy | Plant | CALVERT CLIFFS | 2 | ? |  | 1 | NA | Failure of emergency diesel generator to start during a partial loss of offsite power due to faulty relay. | PWR | Operational | 911 | 1976 |  | 1 | EDG; Power supply: electrical distribution system | 1,2 |  | T | 13 | 20
980 | 6 | 10 | 2009 | Dothan, United States | United States | Energy | Plant | FARLEY | 2 | ? |  | 1 | NA | Standby service water pump unavailable for 23 days. | PWR | Operational | 928 | 1981 |  | 1 | Natural hazard: seismic | 3 | Inadequate design | H | 0 | 1
981 | 9 | 9 | 2010 | Hartsville, United States | United States | Energy | Plant | ROBINSON | 2 | ? |  | 1 | NA | Reactor trip due to a degraded connection on a circuit board in the electro-hydraulic control cabinet. | PWR | Operational | 780 | 1970 |  | 1 | Instrumentation & control: electro-hydraulic (EH) control cabinet | 2? | degraded connection | T | 8 | 11
982 | 1 | 9 | 1996 | Haddam Neck, United States | United States | Energy | Plant | HADDAM NECK | Single | ? |  | 1 | NA | After a Residual Heat Removal Pump Seized, It Was Determined to Be Susceptible to Failure Since Being Overhauled in 1987 | PWR | Permanent Shutdown | 603 | 1967 | <LC> ref/source missing | 1 | RHR | 1 |  | T
983 |  | 2 | 2002 | Buchanan, United States | United States | Energy | Plant | INDIAN POINT | 2 | ? |  | 2 | NA | Degraded control room fire barrier. | PWR | Operational | 1067 | 1973 |  | 1 | Event at auxiliary building: (potential) fire in central control room | 3 | Inadequate maintenance | H | 0 | 1
984 | 18 | 6 | 2005 | Marseilles, United States | United States | Energy | Plant | LASALLE | 1,2 | ? |  | ? | NA | Fouling of the cooling water systems due to concrete sealant injected into the service water tunnel | BWR | Operational | 1207 | 1982;1984 | <LC> ref/source missing | ? |  |  |  | H
985 | 6 | 3 | 1996 | Cornelius, United States | United States | Energy | Plant | MCGUIRE | 2 | ? |  | 1 | NA | 2B Emergency Diesel Generator Inoperable Due to Slow Instrumentation Response | PWR | Operational | 1215 | 1983 |  | 1 | EDG | 1 | Design deficiency | H | 0 | 1
986 | 1 | 5 | 2014 | Waterford, United States | United States | Energy | Plant | MILLSTONE | 3 | ? |  | 1 | NA | Turbine Driven Auxiliary Feedwater Pump Operability Impacted by Incorrect Bearing. | PWR | Operational | 1280 | 1986 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 | Improper maintenance | H | 0 | 0
989 | 21 | 4 | 1997 | Oconee, United States | United States | Energy | Plant | OCONEE | 2,3 | ? |  | 1 | NA | Unisolable reactor coolant system (RCS) leak | PWR | Operational | 891;900 | 1973;1974 |  | 1 | Reactor Coolant System (RCS) | 1 | Inadequate inspection & maintenance | H | 40 | 60
991 | 25 | 9 | 2011 | South Haven, United States | United States | Energy | Plant | PALISADES | Single | ? |  | 1 to 2 | NA | Inadequate work instructions led to the loss of a 125-volt, direct-current train and subsequent reactor trip. | PWR | Operational | 850 | 1971 |  | 1 | Power supply: direct current (DC) electrical distribution (ED) panel | 2? | deficient procedure guidance | H | 10 | 15
992 | 15 | 9 | 2003 | York County, United States | United States | Energy | Plant | PEACH BOTTOM | 2,3 | ? |  | 1 | NA | Plant-centered LOOP, an emergency diesel generator unavailable and stuck open safety relief valve. | BWR | Operational | 1412 | 1974 |  | 1 | Off-Site Electrical Grid Disturbance | 3 |  | T | 15 | 25
993 | 30 | 6 | 1996 | Red Wing, United States | United States | Energy | Plant | PRAIRIE ISLAND | 1,2 | ? |  | 1 to 2 | NA | Loss of Power to Safeguards Buses on Both Units | PWR | Operational | 566;560 | 1973;1974 |  | 1 | Natural hazard: high winds | 3 |  | T | 3 | 10
994 | 10 | 1 | 1996 | Salem, United States | United States | Energy | Plant | SALEM | 1,2 | ? |  | 1 | NA | Charging Pump Suction Valves from the RWST Potentially Unavailable Because of Pressure Locking | PWR | Operational | 1254;1200 | 1976;1981 | <LC> ref/source missing | 1 |  |  |  | ?
995 | 21 | 5 | 1996 | Seabrook, United States | United States | Energy | Plant | SEABROOK | 1 | ? |  | 1 | NA | Turbine-Driven Emergency Feedwater Pump Unavailable Because of a Mechanical Seal Failure | PWR | Operational | 1296 | 1990 |  | 1 | Auxiliary feedwater pump (AFW/EFW) | 1 |  | T?
996 | 8 | 6 | 2010 | Gravel Neck, United States | United States | Energy | Plant | SURRY | 1 | ? |  | 1 | NA | Reactor trip due to loss of electrical bus and additional complications. | PWR | Operational | 890 | 1972 |  | 1 | Power supply: 120 VAC Vital Bus | 1 | Human error | H | 6 | 8
997 | 16 | 7 | 2010 | Salem, United States | United States | Energy | Plant | SUSQUEHANNA | 1 | ? |  | 1 | NA | Manual reactor scram due to leakage from the circulating water system and subsequent flooding of the condenser bay. | BWR | Operational | 1330 | 1982 |  | 1 | circulating water system | 2 | inadequate design & procedure | H | 40 | 70
998 | 22 | 11 | 2009 | Dauphin, United States | United States | Energy | Plant | THREE MILE ISLAND | 1 | ? |  | 0 | NA | The workers did not recognize that the vacuum cleaner lacked a high-efficiency particulate air (HEPA) filter and that it was dispersing airborne radioactivity into the containment building causing alarms on various monitors. No radioactivity was detectable above background outside the containment construction opening. | PWR | Operational | 880 | 1974 |  | 0 | Containment | 1 | Improper maintenance | H | 1 | 10
999 | 21 | 6 | 1997 | Dauphin, United States | United States | Energy | Plant | THREE MILE ISLAND | 1 | ? |  | 1 | NA | Failure of both generator output breakers causes a loss of offiste power (LOOP) | PWR | Operational | 880 | 1974 |  | 1 | Power supply: 230KV substation | 2 | Failed generator breaker | T | 10 | 15
1000 | 29 | 9 | 2003 | Killona, United States | United States | Energy | Plant | WATERFORD | 3 | ? |  | 1 | NA | Degraded EDG due to failed fuel line. | PWR | Operational | 1250 | 1985 |  | 1 | EDG | 1 | Improper maintenance | H | 0 | 1
1001 | 22 | 1 | 1997 | Wiscasset, United States | United States | Energy | Plant | MAINE YANKEE | Single | ? |  | 1 | NA | Reactor coolant system loop fill header motor-operated valve Overpressure | PWR | Permanent Shutdown | 900 | 1972 | <LC> ref/source missing | 1
1002 | 3 | 5 | 1997 | Oconee, United States | United States | Energy | Plant | OCONEE | 3 | ? |  | 1 | NA | High-pressure injection system inoperable due to design deficiency and improper work Practices | PWR | Operational | 900 | 1974 |  | 1 | High Pressure Injection (HPI) | 1 | Design Deficiency & Improper Work Practices | H | 30 | 40
1003 | 2 | 11 | 1997 | Fort Pierce, United States | United States | Energy | Plant | ST. LUCIE | 1 | ? |  | 1 | NA | Nonconservative recirculation actuation signal set point | PWR | Operational | 1045 | 1976 |  | 1 | Engineered Safety Features Actuation System (ESFAS) | 1? |  | H | 0 | 0
1004 | 3 | 7 | 1992 | Fort Calhoun, United States | United States | Energy | Plant | FORT CALHOUN | 1 | ? |  | 2 | NA | Reactor Trip Due to Invertor Malfunction and Subsequent Pressurizer Safety Valve Leak | PWR | Permanent Shutdown | 512 | 1973 |  | 1 | Pressurizer Safety Valve; Power supply: non-safety related inverter | 1,2 |  | T | 15 | 30
1005 | 22 | 8 | 1992 | Hartsville, United States | United States | Energy | Plant | ROBINSON | 2 | ? |  | 2 | NA | Unusual Event Due to Loss of Off-Site Power and Reactor Trip | PWR | Operational | 780 | 1970 |  | 1 | Power supply: Startup Transformer | 2? | Short circuit | T | 0 | 1
1006 | 19 | 10 | 1992 | Oconee, United States | United States | Energy | Plant | OCONEE | 2 | ? |  | 2 | NA | Loss of Off-site Power and Unit Trip Due to Management Deficiencies, Less than Adequate Corrective Action Program | PWR | Operational | 891 | 1973 |  | 1 | Switchyard | 2 | Management Deficiency, Inadequate Corrective Action Program | H | 1 | 10
1007 | 30 | 12 | 1992 | Daisy, United States | United States | Energy | Plant | SEQUOYAH | 1,2 | ? |  | 2 | NA | Reactor Trip as a Result of a Switchyard Power Circuit Breaker Fault and a Unit 2 Entry Into Limiting Condition for Operation [LCO] 3.0.3 when Both Centrifugal Charging Pumps were Removed from Service | PWR | Operational | 1221;1200 | 1980;1981 |  | 1 | Switchyard | 2 |  | T?
1008 | 25 | 2 | 1993 | York County, United States | United States | Energy | Plant | CATAWBA | 1,2 | ? |  | 2 | NA | Technical Specification 3.0.3 Entered Due to Inoperable Pump Discharge Valves | PWR | Operational | 1188 | 1985;1986 |  | 1 | Nuclear service Water (RN) System | 1? |  | T;H | 0 | 0
1009 | 19 | 4 | 1993 | Perry, United States | United States | Energy | Plant | PERRY | 1 | ? |  | 2 | NA | Excessive Strainer Differential Pressure Across the residual heat removal (RHR) Suction Strainer Could Have Compromised Long Term Cooling During Post-LOCA Operation | BWR | Operational | 1303 | 1986 |  | 1 | RHR | 1 | inadequate design and licensing basis control | H | 0 | 0
1010 | 14 | 9 | 1993 | Marseilles, United States | United States | Energy | Plant | LASALLE | 1 | ? |  | 2 | NA | Unit 1 Scram and Loss of Off-Site Power Due to Bus Duct Water Intrusion | BWR | Operational | 1207 | 1982 |  | 1 | Power supply: System Auxiliary Transformer (SAT) | 2? | degraded ductwork joint seals | T | 1 | 10
1011 | 16 | 2 | 1994 | Haddam Neck, United States | United States | Energy | Plant | HADDAM NECK | Single | ? |  | 2 | NA | Automatic 480 Volt Bus Transfer Failure Due to Circuit Breaker Malfunction | PWR | Permanent Shutdown | 603 | 1967 |  | 1 | Power supply: Automatic Bus Transfer (ABT) circuit for Motor Control Center (MCC) | 2 | (possibly) improper maintanence | H? | 0 | 1
1012 | 2 | 8 | 1995 | Fort Pierce, United States | United States | Energy | Plant | ST. LUCIE | 1 | ? |  | 2 | NA | Failed PORVs, Reactor Coolant Pump, Seal Failure, Relief Valve and Subsequent Shutdown Cooling System Unavailability, Plus Other Problems | PWR | Operational | 1045 | 1976 |  | 1 | Power Operated Relief Valves (PORV), Reactor Coolant System (RCS) | 1 | Human error, Lack of Design Margin | H | 0 | 1
1013 | 18 | 3 | 2011 | Doel, Belgium | Belgium | Energy | Plant | DOEL | 4 | 2 | 2 |  | WE | After the replacement of an auxiliary feedwater turbopump during the 2009-outage, the rotational speed of the pump was adjusted to a lower level because of vibration problems with the pump. The pump was tested and requalified according to the technical specifications but the curve (flow-rate pressure) was not verified as required by ASME-XI. The actual flow rate delivered in case of specific accidents could no longer match the flow rate postulated in the safety report. Nevertheless, an independent emergency feedwater system could offer additional capacity in such circumstances. This anomaly was discovered on 18 march 2011 during a test which was suggested by the authorities. | PWR | Operational | 1090 | 1985 | degradation of a safety function | ? |  | 1 |  | H | 0 | 0
1014 | 19 | 1 | 2011 | Alto Lucero, Mexico | Mexico | Energy | Plant | LAGUNA VERDE | 2 | 1 | 2 |  | NA | Operating at 43.2% of rated power in process for testing. While testing for the load rejection signal, the main turbine incremented its speed and main turbine control valves started to close. When the pressure at the first step started to decrease until 4.6 kg/cm2, there was a main turbine trip signal due to the actuation of the Speed Acceleration Limiter, but this signal trip did not actuate the Reactor Primary System (RPS), instead there was a reactor trip due to high pressure signal of the reactor pressure vessel. The cause was that the during the power rising process after testing of the Moisture Separator Reheaters the alarms associated to the bypass of the signal trip for the main turbine trip were not reestablished, therefore the during approximately 40 minutes the reactor operated without this reactor trip signal. | BWR | Operational | 810 | 1994 | degradation of a safety function | 1 |  | 1 |  | H | 0 | 10
1015 | 19 | 3 | 2001 | Cattenom, France | France | Energy | Plant | CATTENOM | 3 | 2 |  | 0 | WE | Ninety-two rods (less than 1% of rods) damaged were discovered during a refueling and 10-year inspection outage; the primary circuit was also highly contaminated. EdF proposed fretting due to rod vibration as reason while the origin of the vibration is still unknown. | PWR | Operational | 1362 | 1990 | Cause not well understood. Omit? | 0 | Fuel rods | 1 |  | ? | 300 | 500
1016 |  | 5 | 2018 | Leibstadt, Switzerland | Switzerland | Energy | Plant | LEIBSTADT | Single |  | 1 |  | WE | As part of a regular test, the operator of the Leibstadt nuclear power plant has found that two valves in the Special Emergency and Heat Removal System (SEHR) were in the wrong position. Instead of being throttled, they were closed. The correct position of the valves would have been critical in requesting the emergency system to cool one of the two main pumps and the associated pump room. | BWR | Operational | 1275 | 1984 |  | 0 | Special Emergency and Heat Removal System (SEHR) | 1 | Malpositioning of valves | H | 0 | 0
[25 empty] | 1079378.97 | 1566212.17
Note on O57: http://www.nrc.gov/reactors/operating/ops-experience/open-phase-electric-systems.html
Note on A200: Panagiotis Kyriakis: desciption has been reviewed by Wolfgang, but it does not match the one given by the sources..?
Note on A214: Panagiotis Kyriakis: problematic cost estimation: not sure how the shutdown of the plant is related to this event. Source 573 mentions that the plant was a top performer and that it had a good and successful operation history and that the onwers voted to shut it down. it doesnt relate the shutdown to this accident. accident itself seems to have had a negligable cost